## PICS
SunSpec PlugFest Protocol Implementation Conformance Statement (PICS)
A PICS is a structured document that asserts which specific requirements are met by a given implementation of a protocol standard.
SunSpec defines information models for components of renewable energy systems based on recommendations of SunSpec members.
The specification contains mappings for the SunSpec logical device types and options.
This PICS specifies the supported logical devices, options, and fixed values provided by a compliant implemenation of the standard
Note that mandatory device attributes are required to be supported by all implementations supporting that logical device.
Instructions
Using your SunSpec C_Manunfacturer ID and product MODEL number, Save this file as: SunSpec_PICS_MANUF_MODEL v1.xlsx
Complete the summary below
For each supported device block for this model, complete the PICS worksheet by marking supported options, fixed values, and events.
You must mark all mandatory values with a 'Y' for Yes/Supported.
Delete any unneeded worksheets
Submit this workbook to pics@sunspec.org
Guide to Model Prefix Abbrevations
A - Aggregator Models
C - Common Models
E - Environmental Models
I - Inverter Models
IC - Inverter Control Models
M- Meter Models
NC - Network Configuration Models
P - Panel Models
SC - String Combiner Models
Summary
Date | Date of Submission
Manuf | Manufacturer Name (Full Name for certificate)
Submiter | Your Name, Email address, phone
Model | Manufacturer model id (as in Common Block)
SunSpec Type | Device, Logger, or Application
Base Register | Base MODBUS register of your device where the SunSpec 32 bit signature (0x53756e53) is found (00000, 40000, 50000 decimal)
Mod Address | MODBUS address of your device
IP Address | Specify the IP address and port for nodes addressable over MODBUS/TCP
SunSpec Block IDs | Specify the SunSpec Model Block IDs supported by this device
Vendor Extension Block IDs | Specify any vendor extension block ids used by this device. Vendor block ids must be registered with SunSpec to be compliant.

## C 001
// 1-Common : All SunSpec compliant devices must include this as the first model ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 2 | 2 | R | SID |  | uint32 |  |  | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map |  | M
3 | 3 | 1 | R | ID |  | unit16 |  |  | A well-known value 1. Uniquely identifies this as a SunSpec Common Model |  | M
4 | 4 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 66 |  | M
// 1 Common Fixed Block (66)
5 | 20 | 16 | R | Mn | Manufacturer | string |  |  | Well known value registered with SunSpec for compliance |  | M
21 | 36 | 16 | R | Md | Model | string |  |  | Manufacturer specific value (32 chars) |  | M
37 | 44 | 8 | R | Opt | Options | string |  |  | Manufacturer specific value (32 chars) |  | O
45 | 52 | 8 | R | Vr | Version | string |  |  | Manufacturer specific value (32 chars) |  | O
53 | 68 | 16 | R | SN | Serial Number | string |  |  | Manufacturer specific value (32 chars) |  | M
69 | 69 | 1 | RW | DA | Device Address | uint16 |  |  | Modbus device address |  | O
70 | 70 | 1 | R | Pad |  | pad |  |  | Force even alignment |  | O

## A 002
// 2-Basic Aggregator : Aggregates a collection of models for a given model id ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 2. Uniquely identifies this as a SunSpec Basic Aggregator Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 14 |  | M
// 2 Basic Aggregator Fixed Block (14)
3 | 3 | 1 | R | AID | AID | uint16 |  |  | Aggregated model id |  | M
4 | 4 | 1 | R | N | N | uint16 |  |  | Number of aggregated models |  | M
5 | 5 | 1 | R | UN | UN | uint16 |  |  | Update Number. Incrementing nunber each time the mappping is changed. If the number is not changed from thelast reading the direct access to a specific offset will result in reading the same logical model as before. Otherwise the entire model must be read to refresh the changes |  | M
6 | 6 | 1 | R | St | Status | enum16 |  |  | Enumerated status code |  | M
7 | 7 | 1 | R | StVnd | Vendor Status | enum16 |  |  | Vendor specific status code |  | O
8 | 9 | 2 | R | Evt | Event Code | bitfield32 |  |  | Bitmask event code |  | M
10 | 11 | 2 | R | EvtVnd | Vendor Event Code | bitfield32 |  |  | Vendor specific event code |  | O
12 | 12 | 1 | R | Ctl | Control | enum16 |  |  | Control register for all aggregated devices |  | O
13 | 14 | 2 | R | CtlVnd | Vendor Control | enum32 |  |  | Vendor control register for all aggregated devices |  | O
15 | 16 | 2 | R | CtlVl | Control Value | enum32 |  |  | Numerical value used as a parameter to the control |  | O
// St enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
OFF |  |  | 1
ON |  |  | 2
FULL |  |  | 3
FAULT |  |  | 4
// Ctl enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NONE |  |  | 0
AUTOMATIC |  |  | 1
FORCE_OFF |  |  | 2
TEST |  |  | 3
THROTTLE |  |  | 4
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
GROUND_FAULT |  |  | 0
INPUT_OVER_VOLTAGE |  |  | 1
RESERVED |  |  | 2
DC_DISCONNECT |  |  | 3
RESERVED |  |  | 4
RESERVED |  |  | 5
MANUAL_SHUTDOWN |  |  | 6
OVER_TEMPERATURE |  |  | 7
RESERVED |  |  | 8
RESERVED |  |  | 9
RESERVED |  |  | 10
RESERVED |  |  | 11
BLOWN_FUSE |  |  | 12
UNDER_TEMPERATURE |  |  | 13
MEMORY_LOSS |  |  | 14
ARC_DETECTION |  |  | 15
THEFT_DETECTION |  |  | 16
OUTPUT_OVER_CURRENT |  |  | 17
OUTPUT_OVER_VOLTAGE |  |  | 18
OUTPUT_UNDER_VOLTAGE |  |  | 19
TEST_FAILED |  |  | 20

## SEC 003
// 3-Secure Dataset Read Operation Model (DRAFT 2) : Compute a digial signature over a specifed set of data registers ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 3. Uniquely identifies this as a SunSpec Secure Dataset Read Operation Model (DRAFT 2) Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 108+N*1 |  | M
// 3 Secure Dataset Read Operation Model (DRAFT 2) Fixed Block (108)
3 | 3 | 1 | RW | X | X | uint16 |  |  | Number of (offset, value) pairs being requested | A max of 50 (offset, value) pairs are allocated | M
4 | 4 | 1 | RW | Off1 | Offset1 | uint16 |  |  | Offset of register to read for Val1 | Unused offsets shall be set to 0xFFFF (unimplemented) | M
5 | 5 | 1 | RW | Off2 |  | uint16 |  |  |  |  | M
6 | 6 | 1 | RW | Off3 |  | uint16 |  |  |  |  | M
7 | 7 | 1 | RW | Off4 |  | uint16 |  |  |  |  | M
8 | 8 | 1 | RW | Off5 |  | uint16 |  |  |  |  | M
9 | 9 | 1 | RW | Off6 |  | uint16 |  |  |  |  | M
10 | 10 | 1 | RW | Off7 |  | uint16 |  |  |  |  | M
11 | 11 | 1 | RW | Off8 |  | uint16 |  |  |  |  | M
12 | 12 | 1 | RW | Off9 |  | uint16 |  |  |  |  | M
13 | 13 | 1 | RW | Off10 |  | uint16 |  |  |  |  | M
14 | 14 | 1 | RW | Off11 |  | uint16 |  |  |  |  | M
15 | 15 | 1 | RW | Off12 |  | uint16 |  |  |  |  | M
16 | 16 | 1 | RW | Off13 |  | uint16 |  |  |  |  | M
17 | 17 | 1 | RW | Off14 |  | uint16 |  |  |  |  | M
18 | 18 | 1 | RW | Off15 |  | uint16 |  |  |  |  | M
19 | 19 | 1 | RW | Off16 |  | uint16 |  |  |  |  | M
20 | 20 | 1 | RW | Off17 |  | uint16 |  |  |  |  | M
21 | 21 | 1 | RW | Off18 |  | uint16 |  |  |  |  | M
22 | 22 | 1 | RW | Off19 |  | uint16 |  |  |  |  | M
23 | 23 | 1 | RW | Off20 |  | uint16 |  |  |  |  | M
24 | 24 | 1 | RW | Off21 |  | uint16 |  |  |  |  | M
25 | 25 | 1 | RW | Off22 |  | uint16 |  |  |  |  | M
26 | 26 | 1 | RW | Off23 |  | uint16 |  |  |  |  | M
27 | 27 | 1 | RW | Off24 |  | uint16 |  |  |  |  | M
28 | 28 | 1 | RW | Off25 |  | uint16 |  |  |  |  | M
29 | 29 | 1 | RW | Off26 |  | uint16 |  |  |  |  | M
30 | 30 | 1 | RW | Off27 |  | uint16 |  |  |  |  | M
31 | 31 | 1 | RW | Off28 |  | uint16 |  |  |  |  | M
32 | 32 | 1 | RW | Off29 |  | uint16 |  |  |  |  | M
33 | 33 | 1 | RW | Off30 |  | uint16 |  |  |  |  | M
34 | 34 | 1 | RW | Off31 |  | uint16 |  |  |  |  | M
35 | 35 | 1 | RW | Off32 |  | uint16 |  |  |  |  | M
36 | 36 | 1 | RW | Off33 |  | uint16 |  |  |  |  | M
37 | 37 | 1 | RW | Off34 |  | uint16 |  |  |  |  | M
38 | 38 | 1 | RW | Off35 |  | uint16 |  |  |  |  | M
39 | 39 | 1 | RW | Off36 |  | uint16 |  |  |  |  | M
40 | 40 | 1 | RW | Off37 |  | uint16 |  |  |  |  | M
41 | 41 | 1 | RW | Off38 |  | uint16 |  |  |  |  | M
42 | 42 | 1 | RW | Off39 |  | uint16 |  |  |  |  | M
43 | 43 | 1 | RW | Off40 |  | uint16 |  |  |  |  | M
44 | 44 | 1 | RW | Off41 |  | uint16 |  |  |  |  | M
45 | 45 | 1 | RW | Off42 |  | uint16 |  |  |  |  | M
46 | 46 | 1 | RW | Off43 |  | uint16 |  |  |  |  | M
47 | 47 | 1 | RW | Off44 |  | uint16 |  |  |  |  | M
48 | 48 | 1 | RW | Off45 |  | uint16 |  |  |  |  | M
49 | 49 | 1 | RW | Off46 |  | uint16 |  |  |  |  | M
50 | 50 | 1 | RW | Off47 |  | uint16 |  |  |  |  | M
51 | 51 | 1 | RW | Off48 |  | uint16 |  |  |  |  | M
52 | 52 | 1 | RW | Off49 |  | uint16 |  |  |  |  | M
53 | 53 | 1 | RW | Off50 |  | uint16 |  |  |  |  | M
54 | 54 | 1 | W | Sgn | Sign | enum16 |  |  | A write to this register causes the data set to be updated according to X and the requested offsets, timestamped, and signed. |  | M
55 | 55 | 1 | R | Val1 | Value1 | uint16 |  |  | Copy of value from register Off1. | Unused values shall return 0xFFFF (unimplemented) | M
56 | 56 | 1 | R | Val2 |  | uint16 |  |  |  |  | M
57 | 57 | 1 | R | Val3 |  | uint16 |  |  |  |  | M
58 | 58 | 1 | R | Val4 |  | uint16 |  |  |  |  | M
59 | 59 | 1 | R | Val5 |  | uint16 |  |  |  |  | M
60 | 60 | 1 | R | Val6 |  | uint16 |  |  |  |  | M
61 | 61 | 1 | R | Val7 |  | uint16 |  |  |  |  | M
62 | 62 | 1 | R | Val8 |  | uint16 |  |  |  |  | M
63 | 63 | 1 | R | Val9 |  | uint16 |  |  |  |  | M
64 | 64 | 1 | R | Val10 |  | uint16 |  |  |  |  | M
65 | 65 | 1 | R | Val11 |  | uint16 |  |  |  |  | M
66 | 66 | 1 | R | Val12 |  | uint16 |  |  |  |  | M
67 | 67 | 1 | R | Val13 |  | uint16 |  |  |  |  | M
68 | 68 | 1 | R | Val14 |  | uint16 |  |  |  |  | M
69 | 69 | 1 | R | Val15 |  | uint16 |  |  |  |  | M
70 | 70 | 1 | R | Val16 |  | uint16 |  |  |  |  | M
71 | 71 | 1 | R | Val17 |  | uint16 |  |  |  |  | M
72 | 72 | 1 | R | Val18 |  | uint16 |  |  |  |  | M
73 | 73 | 1 | R | Val19 |  | uint16 |  |  |  |  | M
74 | 74 | 1 | R | Val20 |  | uint16 |  |  |  |  | M
75 | 75 | 1 | R | Val21 |  | uint16 |  |  |  |  | M
76 | 76 | 1 | R | Val22 |  | uint16 |  |  |  |  | M
77 | 77 | 1 | R | Val23 |  | uint16 |  |  |  |  | M
78 | 78 | 1 | R | Val24 |  | uint16 |  |  |  |  | M
79 | 79 | 1 | R | Val25 |  | uint16 |  |  |  |  | M
80 | 80 | 1 | R | Val26 |  | uint16 |  |  |  |  | M
81 | 81 | 1 | R | Val27 |  | uint16 |  |  |  |  | M
82 | 82 | 1 | R | Val28 |  | uint16 |  |  |  |  | M
83 | 83 | 1 | R | Val29 |  | uint16 |  |  |  |  | M
84 | 84 | 1 | R | Val30 |  | uint16 |  |  |  |  | M
85 | 85 | 1 | R | Val31 |  | uint16 |  |  |  |  | M
86 | 86 | 1 | R | Val32 |  | uint16 |  |  |  |  | M
87 | 87 | 1 | R | Val33 |  | uint16 |  |  |  |  | M
88 | 88 | 1 | R | Val34 |  | uint16 |  |  |  |  | M
89 | 89 | 1 | R | Val35 |  | uint16 |  |  |  |  | M
90 | 90 | 1 | R | Val36 |  | uint16 |  |  |  |  | M
91 | 91 | 1 | R | Val37 |  | uint16 |  |  |  |  | M
92 | 92 | 1 | R | Val38 |  | uint16 |  |  |  |  | M
93 | 93 | 1 | R | Val39 |  | uint16 |  |  |  |  | M
94 | 94 | 1 | R | Val40 |  | uint16 |  |  |  |  | M
95 | 95 | 1 | R | Val41 |  | uint16 |  |  |  |  | M
96 | 96 | 1 | R | Val42 |  | uint16 |  |  |  |  | M
97 | 97 | 1 | R | Val43 |  | uint16 |  |  |  |  | M
98 | 98 | 1 | R | Val44 |  | uint16 |  |  |  |  | M
99 | 99 | 1 | R | Val45 |  | uint16 |  |  |  |  | M
100 | 100 | 1 | R | Val46 |  | uint16 |  |  |  |  | M
101 | 101 | 1 | R | Val47 |  | uint16 |  |  |  |  | M
102 | 102 | 1 | R | Val48 |  | uint16 |  |  |  |  | M
103 | 103 | 1 | R | Val49 |  | uint16 |  |  |  |  | M
104 | 104 | 1 | R | Val50 |  | uint16 |  |  |  |  | M
105 | 106 | 2 | R | Tms | Timestamp | uint32 |  |  | Timestamp value is the number of seconds since January 1, 2000 |  | M
107 | 107 | 1 | R | Millis | Milliseconds | uint16 |  |  | Millisecond counter 0-999 |  | M
108 | 108 | 1 | R | Alm | Alarm | enum16 |  |  | Bitmask alarm code |  | M
109 | 109 | 1 | R | Alg | Algorithm | enum16 |  |  | Algorithm used to compute the digital signature | For future proof | M
110 | 110 | 1 | R | N | N | uint16 |  |  | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits) | M
// 3 Secure Dataset Read Operation Model (DRAFT 2) Repeating Block (1)
111 | 111 | 1 | R | DS | DS | uint16 |  |  | Digital Signature | The DS covers all registers from X to N and is N registers in length | M
// Sgn enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
START |  |  | 1 |  | Start |  | Start the secure read operation to populate the dataset and produce the digital signature
// Alm enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NONE |  |  | 0 |  | NONE |  | No Alarms
ALM |  |  | 1 |  | ALARM |  | Security Alarm
// Alg enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NONE |  |  | 0 |  | NONE |  | No digital signature |  | For test purposes only
AES-GMAC-64 |  |  | 1 |  | AES-GMAC-64 |  | 64 bit AES signature algorithm is used

## SEC 004
// 4-Secure Write Operation Model (DRAFT 1) : Include a digial signature along with the control data ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 4. Uniquely identifies this as a SunSpec Secure Write Operation Model (DRAFT 1) Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 106+N*1 |  | M
// 4 Secure Write Operation Model (DRAFT 1) Fixed Block (106)
3 | 3 | 1 | W | Ctl | Ctl | enum16 |  |  | A write to this register causes the write operation to be committed. |  | M
4 | 4 | 1 | R | Sts | Status | enum16 |  |  | Status of last write operation |  | M
5 | 5 | 1 | RW | X | X | uint16 |  |  | Number of (offset, value) pairs being written | A max of 50 (offset, value) pairs are allocated | M
6 | 6 | 1 | RW | Off1 | Offset1 | uint16 |  |  | Offset of control register to write value to |  | M
7 | 7 | 1 | RW | Val1 | Value1 | uint16 |  |  | Value to write to control register at offset |  | M
8 | 8 | 1 | RW | Off2 |  | uint16 |  |  |  |  | M
9 | 9 | 1 | RW | Val2 |  | uint16 |  |  |  |  | M
10 | 10 | 1 | RW | Off3 |  | uint16 |  |  |  |  | M
11 | 11 | 1 | RW | Val3 |  | uint16 |  |  |  |  | M
12 | 12 | 1 | RW | Off4 |  | uint16 |  |  |  |  | M
13 | 13 | 1 | RW | Val4 |  | uint16 |  |  |  |  | M
14 | 14 | 1 | RW | Off5 |  | uint16 |  |  |  |  | M
15 | 15 | 1 | RW | Val5 |  | uint16 |  |  |  |  | M
16 | 16 | 1 | RW | Off6 |  | uint16 |  |  |  |  | M
17 | 17 | 1 | RW | Val6 |  | uint16 |  |  |  |  | M
18 | 18 | 1 | RW | Off7 |  | uint16 |  |  |  |  | M
19 | 19 | 1 | RW | Val7 |  | uint16 |  |  |  |  | M
20 | 20 | 1 | RW | Off8 |  | uint16 |  |  |  |  | M
21 | 21 | 1 | RW | Val8 |  | uint16 |  |  |  |  | M
22 | 22 | 1 | RW | Off9 |  | uint16 |  |  |  |  | M
23 | 23 | 1 | RW | Val9 |  | uint16 |  |  |  |  | M
24 | 24 | 1 | RW | Off10 |  | uint16 |  |  |  |  | M
25 | 25 | 1 | RW | Val10 |  | uint16 |  |  |  |  | M
26 | 26 | 1 | RW | Off11 |  | uint16 |  |  |  |  | M
27 | 27 | 1 | RW | Val11 |  | uint16 |  |  |  |  | M
28 | 28 | 1 | RW | Off12 |  | uint16 |  |  |  |  | M
29 | 29 | 1 | RW | Val12 |  | uint16 |  |  |  |  | M
30 | 30 | 1 | RW | Off13 |  | uint16 |  |  |  |  | M
31 | 31 | 1 | RW | Val13 |  | uint16 |  |  |  |  | M
32 | 32 | 1 | RW | Off14 |  | uint16 |  |  |  |  | M
33 | 33 | 1 | RW | Val14 |  | uint16 |  |  |  |  | M
34 | 34 | 1 | RW | Off15 |  | uint16 |  |  |  |  | M
35 | 35 | 1 | RW | Val15 |  | uint16 |  |  |  |  | M
36 | 36 | 1 | RW | Off16 |  | uint16 |  |  |  |  | M
37 | 37 | 1 | RW | Val16 |  | uint16 |  |  |  |  | M
38 | 38 | 1 | RW | Off17 |  | uint16 |  |  |  |  | M
39 | 39 | 1 | RW | Val17 |  | uint16 |  |  |  |  | M
40 | 40 | 1 | RW | Off18 |  | uint16 |  |  |  |  | M
41 | 41 | 1 | RW | Val18 |  | uint16 |  |  |  |  | M
42 | 42 | 1 | RW | Off19 |  | uint16 |  |  |  |  | M
43 | 43 | 1 | RW | Val19 |  | uint16 |  |  |  |  | M
44 | 44 | 1 | RW | Off20 |  | uint16 |  |  |  |  | M
45 | 45 | 1 | RW | Val20 |  | uint16 |  |  |  |  | M
46 | 46 | 1 | RW | Off21 |  | uint16 |  |  |  |  | M
47 | 47 | 1 | RW | Val21 |  | uint16 |  |  |  |  | M
48 | 48 | 1 | RW | Off22 |  | uint16 |  |  |  |  | M
49 | 49 | 1 | RW | Val22 |  | uint16 |  |  |  |  | M
50 | 50 | 1 | RW | Off23 |  | uint16 |  |  |  |  | M
51 | 51 | 1 | RW | Val23 |  | uint16 |  |  |  |  | M
52 | 52 | 1 | RW | Off24 |  | uint16 |  |  |  |  | M
53 | 53 | 1 | RW | Val24 |  | uint16 |  |  |  |  | M
54 | 54 | 1 | RW | Off25 |  | uint16 |  |  |  |  | M
55 | 55 | 1 | RW | Val25 |  | uint16 |  |  |  |  | M
56 | 56 | 1 | RW | Off26 |  | uint16 |  |  |  |  | M
57 | 57 | 1 | RW | Val26 |  | uint16 |  |  |  |  | M
58 | 58 | 1 | RW | Off27 |  | uint16 |  |  |  |  | M
59 | 59 | 1 | RW | Val27 |  | uint16 |  |  |  |  | M
60 | 60 | 1 | RW | Off28 |  | uint16 |  |  |  |  | M
61 | 61 | 1 | RW | Val28 |  | uint16 |  |  |  |  | M
62 | 62 | 1 | RW | Off29 |  | uint16 |  |  |  |  | M
63 | 63 | 1 | RW | Val29 |  | uint16 |  |  |  |  | M
64 | 64 | 1 | RW | Off30 |  | uint16 |  |  |  |  | M
65 | 65 | 1 | RW | Val30 |  | uint16 |  |  |  |  | M
66 | 66 | 1 | RW | Off31 |  | uint16 |  |  |  |  | M
67 | 67 | 1 | RW | Val31 |  | uint16 |  |  |  |  | M
68 | 68 | 1 | RW | Off32 |  | uint16 |  |  |  |  | M
69 | 69 | 1 | RW | Val32 |  | uint16 |  |  |  |  | M
70 | 70 | 1 | RW | Off33 |  | uint16 |  |  |  |  | M
71 | 71 | 1 | RW | Val33 |  | uint16 |  |  |  |  | M
72 | 72 | 1 | RW | Off34 |  | uint16 |  |  |  |  | M
73 | 73 | 1 | RW | Val34 |  | uint16 |  |  |  |  | M
74 | 74 | 1 | RW | Off35 |  | uint16 |  |  |  |  | M
75 | 75 | 1 | RW | Val35 |  | uint16 |  |  |  |  | M
76 | 76 | 1 | RW | Off36 |  | uint16 |  |  |  |  | M
77 | 77 | 1 | RW | Val36 |  | uint16 |  |  |  |  | M
78 | 78 | 1 | RW | Off37 |  | uint16 |  |  |  |  | M
79 | 79 | 1 | RW | Val37 |  | uint16 |  |  |  |  | M
80 | 80 | 1 | RW | Off38 |  | uint16 |  |  |  |  | M
81 | 81 | 1 | RW | Val38 |  | uint16 |  |  |  |  | M
82 | 82 | 1 | RW | Off39 |  | uint16 |  |  |  |  | M
83 | 83 | 1 | RW | Val39 |  | uint16 |  |  |  |  | M
84 | 84 | 1 | RW | Off40 |  | uint16 |  |  |  |  | M
85 | 85 | 1 | RW | Val40 |  | uint16 |  |  |  |  | M
86 | 86 | 1 | RW | Off41 |  | uint16 |  |  |  |  | M
87 | 87 | 1 | RW | Val41 |  | uint16 |  |  |  |  | M
88 | 88 | 1 | RW | Off42 |  | uint16 |  |  |  |  | M
89 | 89 | 1 | RW | Val42 |  | uint16 |  |  |  |  | M
90 | 90 | 1 | RW | Off43 |  | uint16 |  |  |  |  | M
91 | 91 | 1 | RW | Val43 |  | uint16 |  |  |  |  | M
92 | 92 | 1 | RW | Off44 |  | uint16 |  |  |  |  | M
93 | 93 | 1 | RW | Val44 |  | uint16 |  |  |  |  | M
94 | 94 | 1 | RW | Off45 |  | uint16 |  |  |  |  | M
95 | 95 | 1 | RW | Val45 |  | uint16 |  |  |  |  | M
96 | 96 | 1 | RW | Off46 |  | uint16 |  |  |  |  | M
97 | 97 | 1 | RW | Val46 |  | uint16 |  |  |  |  | M
98 | 98 | 1 | RW | Off47 |  | uint16 |  |  |  |  | M
99 | 99 | 1 | RW | Val47 |  | uint16 |  |  |  |  | M
100 | 100 | 1 | RW | Off48 |  | uint16 |  |  |  |  | M
101 | 101 | 1 | RW | Val48 |  | uint16 |  |  |  |  | M
102 | 102 | 1 | RW | Off49 |  | uint16 |  |  |  |  | M
103 | 103 | 1 | RW | Val49 |  | uint16 |  |  |  |  | M
104 | 104 | 1 | RW | Off50 |  | uint16 |  |  |  |  | M
105 | 105 | 1 | RW | Val50 |  | uint16 |  |  |  |  | M
106 | 106 | 1 | RW | Role | Role | uint16 |  |  | Signing key used 0-5 | Each controller is assigned a key index that maps to their access control role | M
107 | 107 | 1 | RW | Alg | Algorithm | enum16 |  |  | Algorithm used to compute the digital signature | For future proof | M
108 | 108 | 1 | RW | N | N | uint16 |  |  | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits) | M
// 4 Secure Write Operation Model (DRAFT 1) Repeating Block (1)
109 | 109 | 1 | RW | DS | DS | uint16 |  |  | Digital Signature | The DS covers all registers from X to N and is N registers in length | O
// Ctl enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NOP |  |  | 0
COMMIT |  |  | 1
// Sts enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
SUCCESS |  |  | 0 |  | SUCCESS |  | Operation succeeded
DS |  |  | 1 |  | DS |  | Operation failed digital signature check
ACL |  |  | 2 |  | ACL |  | Operation failed access control check |  | One or more registers were not writable by this role
OFF |  |  | 3 |  | OFF |  | Operation failed offset check |  | Offset out of range or missing from multi-register value
VAL |  |  | 4 |  | VAL |  | Operation failed valid value check |  | Value is out of acceptable range
// Alg enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NONE |  |  | 0 |  | NONE |  | No digital signature |  | For test purposes only
AES-GMAC-64 |  |  | 1 |  | AES-GMAC-64 |  | 64 bit AES signature algorithm is used

## NC 010
// 10-Communication Interface Header : To be included first for a complete interface description ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 10. Uniquely identifies this as a SunSpec Communication Interface Header Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 4 |  | M
// 10 Communication Interface Header Fixed Block (4)
3 | 3 | 1 | R | St | Interface Status | enum16 |  |  | Overall interface status |  | M
4 | 4 | 1 | RW | Ctl | Interface Control | uint16 |  |  | Overall interface control (TBD) |  | O
5 | 5 | 1 | R | Typ | Physical Access Type | enum16 |  |  | Enumerated value. Type of physical media |  | O
6 | 6 | 1 | R | Pad |  | pad |  |  |  |  | O
// St enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
DOWN |  |  | 0 |  | down |  | Interface is down
UP |  |  | 1 |  | up |  | Interface is up
FAULT |  |  | 2 |  | fault |  | Interface is in a fault state
// Typ enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
UNKNOWN |  |  | 0 |  | unknown |  | Unkown media
INTERNAL |  |  | 1 |  | internal |  | Internal e.g. embbedded switch
TWISTED_PAIR |  |  | 2 |  | twisted pair |  | Twisted Pair
FIBER |  |  | 3 |  | fiber |  | Fiber
WIRELESS |  |  | 4

## NC 011
// 11-Ethernet Link Layer : Include to support a wired ethernet port ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 10 |  | M
// 11 Ethernet Link Layer Fixed Block (10)
3 | 3 | 1 | R | Spd | Ethernet Link Speed | uint16 | Mbps |  | Interface speed in Mb/s |  | M
4 | 4 | 1 | R | CfgSt | Interface Status Flags | bitfield16 |  |  | Bitmask values Interface flags. |  | M
5 | 5 | 1 | R | St | Link State | enum16 |  |  | Enumerated value. State information for this interface |  | M
6 | 6 | 1 | R | MAC | MAC | uint16 |  |  | IEEE MAC address of this interface |  | O
7 | 10 | 4 | RW | Nam | Name | string |  |  | Interface name (8 chars) |  | O
11 | 11 | 1 | RW | Ctl | Control | bitfield16 |  |  | Control flags |  | O
12 | 12 | 1 | RW | FrcSpd | Forced Speed | uint16 | Mbps |  | Forced interface speed in Mb/s when AUTO is disabled |  | O
// St enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
UNKNOWN |  |  | 0 |  | unknown |  | Unknown state
ENABLED |  |  | 1 |  | enabled |  | Link is enabled and read
DISABLED |  |  | 2 |  | disabled |  | Link is disabled
TESTING |  |  | 3 |  | testing |  | Link is in test
// CfgSt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
LINK |  |  | 0 |  | link status |  | link is up
FULL_DUPLEX |  |  | 1 |  | full duplex |  | link is in full duplex mode
AUTO_NEG1 |  |  | 2 |  | auto negotiation 1 |  | Auto-negotiation bits are encoded as: 000 - inprogress. 001 - speed detection has failed. 010 - negotiation has failed. 011 - negotiated speed and duplex. 100 - negotiation not attempted.
AUTO_NEG2 |  |  | 3 |  | auto negotiation 2 |  | See AUTO_NEG1
AUTO_NEG3 |  |  | 4 |  | auto negotiation 3 |  | See AUTO_NEG1
RESET_REQUIRED |  |  | 5 |  | reset required |  | Setting requires reset
HW_FAULT |  |  | 6 |  | hw fault |  | Hardware fault
// Ctl bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
AUTO |  |  | 0 |  | auto |  | Enable auto-negotiatition
FULL_DUPLEX |  |  | 1 |  | duplex |  | Force full duplex

## NC 012
// 12-IPv4 : Include to support an IPv4 protocol stack on this interface ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 98 |  | M
// 12 IPv4 Fixed Block (98)
3 | 6 | 4 | RW | Nam | Name | string |  |  | Interface name |  | O
7 | 7 | 1 | R | CfgSt | Config Status | enum16 |  |  | Enumerated value. Configuration status |  | M
8 | 8 | 1 | R | ChgSt | Change Status | bitfield16 |  |  | Bitmask value. A configuration change is pending |  | M
9 | 9 | 1 | R | Cap | Config Capability | bitfield16 |  |  | Bitmask value. Identify capable sources of configuration |  | M
10 | 10 | 1 | RW | Cfg | IPv4 Config | enum16 |  |  | Enumerated value. Configuration method used. |  | M
11 | 11 | 1 | RW | Ctl | Control | enum16 |  |  | Configure use of services |  | M
12 | 19 | 8 | RW | Addr | IP | string |  |  | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx |  | M
20 | 27 | 8 | RW | Msk | Netmask | string |  |  | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx |  | M
28 | 35 | 8 | RW | Gw | Gateway | string |  |  | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx |  | O
36 | 43 | 8 | RW | DNS1 | DNS1 | string |  |  | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx |  | O
44 | 51 | 8 | RW | DNS2 | DNS2 | string |  |  | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx |  | O
52 | 63 | 12 | RW | NTP1 | NTP1 | string |  |  | IPv4 numeric NTP address as a dotted string xxx.xxx.xxx.xxx |  | O
64 | 75 | 12 | RW | NTP2 | NTP2 | string |  |  | IPv4 numeric NTP address as a dotted string xxx.xxx.xxx.xxx |  | O
76 | 87 | 12 | RW | DomNam | Domain | string |  |  | Domain name (24 chars max) |  | O
88 | 99 | 12 | RW | HostNam | Host Name | string |  |  | Host name (24 chars max) |  | O
100 | 100 | 1 | R | Pad |  | pad |  |  |  |  | O
// CfgSt enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NOT_CONFIGURED |  |  | 0 |  | not configured |  | the stack is not configured
VALID_SETTING |  |  | 1 |  | valid setting |  | a valid configuration from BOOTP, DHCP, or NV mem
VALID_HW |  |  | 2 |  | valid hardware |  | a valid configuration from hardware settings
// Cfg enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
STATIC |  |  | 0 |  | static |  | Use static IP
DHCP |  |  | 1 |  | DHCP |  | Use DHCP
BOOTP |  |  | 2 |  | BOOTP |  | Use BOOTP
ZEROCONF |  |  | 3 |  | zeroconf |  | Use Zeroconf
// Ctl enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLE_DNS |  |  | 0 |  | DNS |  | Enable DNS
ENABLE_NTP |  |  | 1 |  | NTP |  | Enable NTP
// ChgSt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
PENDING |  |  | 0 |  | pending |  | a configuration change is pending
// Cap bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
DHCP |  |  | 0 |  | DHCP |  | DHCP Client capable
BOOTP |  |  | 1 |  | BOOTP |  | BOOTP client capable
ZEROCONF |  |  | 2 |  | zeroconf |  | Zeroconf capable
DNS |  |  | 3 |  | DNS |  | DNS Client capable
CFG_SETTABLE |  |  | 4 |  | configurable |  | Settable configuration capable
HW_CONFIG |  |  | 5 |  | hw |  | Hardware configuration capable
NTP_CLIENT |  |  | 6 |  | ntp |  | NTP Client capable
RESET_REQUIRED |  |  | 7 |  | reset required |  | configuration change requires reset

## NC 013
// 13-IPv6 : Include to support an IPv6 protocol stack on this interface ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 13. Uniquely identifies this as a SunSpec IPv6 Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 174 |  | M
// 13 IPv6 Fixed Block (174)
3 | 6 | 4 | RW | Nam | Name | string |  |  | Interface name |  | O
7 | 7 | 1 | R | CfgSt | Config Status | enum16 |  |  | Enumerated value. Configuration status |  | M
8 | 8 | 1 | R | ChgSt | Change Status | bitfield16 |  |  | Bitmask value. A configuration change is pending |  | M
9 | 9 | 1 | R | Cap | Config Capability | bitfield16 |  |  | Bitmask value. Identify capable sources of configuration |  | M
10 | 10 | 1 | RW | Cfg | IPv6 Config | enum16 |  |  | Enumerated value. Configuration method used. |  | M
11 | 11 | 1 | RW | Ctl | Control | enum16 |  |  | Bitmask value. Configure use of services |  | M
12 | 31 | 20 | RW | Addr | IP | string |  |  | IPv6 numeric address as a dotted string xxxx.xxxx.xxxx.xxxx |  | M
32 | 51 | 20 | RW | CIDR | CIDR | string |  |  | Classless Inter-Domain Routing Number |  | O
52 | 71 | 20 | RW | Gw | Gateway | string |  |  | IPv6 numeric address as a dotted string xxxx.xxxx.xxxx.xxxx |  | O
72 | 91 | 20 | RW | DNS1 | DNS1 | string |  |  | IPv6 numeric DNS address as a dotted string xxxx.xxxx.xxxx.xxxx |  | O
92 | 111 | 20 | RW | DNS2 | DNS2 | string |  |  | IPv6 numeric DNS address as a dotted string xxxx.xxxx.xxxx.xxxx |  | O
112 | 131 | 20 | RW | NTP1 | NTP1 | string |  |  | IPv6 numeric NTP address as a name or dotted string xxxx.xxxx.xxxx.xxxx |  | O
132 | 151 | 20 | RW | NTP2 | NTP2 | string |  |  | IPv6 numeric NTP address as a name or dotted string xxxx.xxxx.xxxx.xxxx |  | O
152 | 163 | 12 | RW | DomNam | Domain | string |  |  | Domain name (24 chars max) |  | O
164 | 175 | 12 | RW | HostNam | Host Name | string |  |  | Host name (24 chars max) |  | O
176 | 176 | 1 | R | Pad |  | pad |  |  |  |  | O
// CfgSt enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NOT_CONFIGURED |  |  | 0 |  | not configured |  | the stack is not configured
VALID_SETTING |  |  | 1 |  | valid setting |  | a valid configuration from BOOTP, DHCP, or NV mem
VALID_HW |  |  | 2 |  | valid hardware |  | a valid configuration from hardware settings
// Cfg enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
STATIC |  |  | 0 |  | static |  | Use static IP
DHCP |  |  | 1 |  | DHCP |  | Use DHCP
BOOTP |  |  | 2 |  | BOOTP |  | Use BOOTP
ZEROCONF |  |  | 3 |  | zeroconf |  | Use Zeroconf
// Ctl enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLE_DNS |  |  | 0 |  | DNS |  | Enable DNS
ENABLE_NTP |  |  | 1 |  | NTP |  | Enable NTP
// ChgSt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
PENDING |  |  | 0 |  | pending |  | a configuration change is pending
// Cap bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
DHCP |  |  | 0 |  | DHCP |  | DHCP Client capable
BOOTP |  |  | 1 |  | BOOTP |  | BOOTP client capable
ZEROCONF |  |  | 2 |  | zeroconf |  | Zeroconf capable
DNS |  |  | 3 |  | DNS |  | DNS Client capable
CFG_SETTABLE |  |  | 4 |  | configurable |  | Settable configuration capable
HW_CONFIG |  |  | 5 |  | hw |  | Hardware configuration capable
NTP_CLIENT |  |  | 6 |  | ntp |  | NTP Client capable
RESET_REQUIRED |  |  | 7 |  | reset required |  | configuration change requires reset

## NC 014
// 14-Proxy Server : Include this block to allow for a proxy server ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 14. Uniquely identifies this as a SunSpec Proxy Server Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 52 |  | M
// 14 Proxy Server Fixed Block (52)
3 | 6 | 4 | RW | Nam | name | string |  |  | Interface name (8 chars) |  | O
7 | 7 | 1 | RW | Cap | Capabilities | bitfield16 |  |  | Bitmask value. Proxy configuration capabilites |  | M
8 | 8 | 1 | RW | Cfg | Config | enum16 |  |  | Enumerated value. Set proxy address type |  | M
9 | 9 | 1 | RW | Typ | Type | bitfield16 |  |  | Enumerate value. Proxy server type |  | M
10 | 29 | 20 | RW | Addr | Address | string |  |  | IPv4 or IPv6 proxy hostname or dotteed address (40 chars) |  | M
30 | 30 | 1 | RW | Port | Port | uint16 |  |  | Proxy port number |  | M
31 | 42 | 12 | RW | User | Username | string |  |  | Proxy user name |  | O
43 | 54 | 12 | RW | Pw | Password | string |  |  | Proxy password |  | O
// Cap bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NO_PROXY |  |  | 0 |  | No Proxy |  | Turn off the proxy
IPV4_PROXY |  |  | 1 |  | IPv4 Proxy |  | Can proxy IPv4
IPV6_PROXY |  |  | 2 |  | IPv6 Proxy |  | Can proxy IPv6

## NC 015
// 15-Interface Counters Model : Interface counters ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 15. Uniquely identifies this as a SunSpec Interface Counters Model Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 24 |  | M
// 15 Interface Counters Model Fixed Block (24)
3 | 3 | 1 | RW | Clr | Clear | uint16 |  |  | Write a "1" to clear all counters |  | O
4 | 5 | 2 | R | InCnt | Input Count | acc32 |  |  | Number of bytes received |  | O
6 | 7 | 2 | R | InUcCnt | Input Unicast Count | acc32 |  |  | Number of Unicast packets received |  | O
8 | 9 | 2 | R | InNUcCnt | Input Non-Unicast Count | acc32 |  |  | Number of non-Unicast packets received |  | O
10 | 11 | 2 | R | InDscCnt | Input Discarded Count | acc32 |  |  | Number of inbound packets received on the interface but discarded |  | O
12 | 13 | 2 | R | InErrCnt | Input Error Count | acc32 |  |  | Number of inbound packets that contain errors (excluding discards) |  | O
14 | 15 | 2 | R | InUnkCnt | Input Unknown Count | acc32 |  |  | Number of inbound packets with unknown protocol |  | O
16 | 17 | 2 | R | OutCnt | Output Count | acc32 |  |  | Total number of bytes transmitted on this interface |  | O
18 | 19 | 2 | R | OutUcCnt | Output Unicast Count | acc32 |  |  | Number of Unicast packets transmitted |  | O
20 | 21 | 2 | R | OutNUcCnt | Output Non-Unicast Count | acc32 |  |  | Number of Non-Unicast packets transmitted |  | O
22 | 23 | 2 | R | OutDscCnt | Output Discarded Count | acc32 |  |  | Number of Discarded output packets |  | O
24 | 25 | 2 | R | OutErrCnt | Output Error Count | acc32 |  |  | Number of outbound error packets |  | O
26 | 26 | 1 | R | Pad |  | pad |  |  |  |  | O

## NC 016
// 16-Simple IP Network : Include this model for a simple IPv4 network stack ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 16. Uniquely identifies this as a SunSpec Simple IP Network Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 52 |  | M
// 16 Simple IP Network Fixed Block (52)
3 | 6 | 4 | RW | Nam | Name | string |  |  | Interface name. (8 chars) |  | O
7 | 7 | 1 | R | Cfg | Config | enum16 |  |  | Enumerated value. Force IPv4 configuration method |  | M
8 | 8 | 1 | RW | Ctl | Control | enum16 |  |  | Bitmask value Configure use of services |  | M
9 | 16 | 8 | RW | Addr | Address | string |  |  | IP addreess |  | M
17 | 24 | 8 | RW | Msk | Netmask | string |  |  | Netmask |  | M
25 | 32 | 8 | RW | Gw | Gateway | string |  |  | Gateway IP address |  | O
33 | 40 | 8 | RW | DNS1 | DNS1 | string |  |  | 32 bit IP address of DNS server |  | O
41 | 48 | 8 | RW | DNS2 | DNS2 | string |  |  | 32 bit IP address of DNS server |  | O
49 | 52 | 4 | R | MAC | MAC | uint64 |  |  | IEEE MAC address of this interface |  | O
53 | 53 | 1 | RW | LnkCtl | Link Control | bitfield16 |  |  | Bitmask value. Link control flags |  | O
54 | 54 | 1 | R | Pad |  | pad |  |  |  |  | O
// Cfg enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
STATIC |  |  | 0 |  | static |  | A static IP address is assigned
DHCP |  |  | 1 |  | DHCP |  | Use DHCP to acquire an IP address
// Ctl enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLE_DNS |  |  | 0 |  | DNS |  | Enable DNS use
ENABLE_NTP |  |  | 1 |  | NTP |  | Enable NTP use
// LnkCtl bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
AUTONEGOTIATE |  |  | 0 |  | auto-negotiate |  | Enable auto-negotiation
FULL_DUPLEX |  |  | 1 |  | full duplex |  | Force full duplex operation
FORCE_10MB |  |  | 2 |  | 10Mbs |  | Force 10 Mb/s link speed
FORCE_1GB |  |  | 3 |  | 1Gbs |  | Force 1 Gb/s link speed

## NC 017
// 17-Serial Interface : Include this model for serial interface configuration support ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 17. Uniquely identifies this as a SunSpec Serial Interface Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 12 |  | M
// 17 Serial Interface Fixed Block (12)
3 | 6 | 4 | RW | Nam | Name | string |  |  | Interface name (8 chars) |  | O
7 | 8 | 2 | RW | Rte | Rate | uint32 | bps |  | Interface baud rate in bits per second |  | M
9 | 9 | 1 | RW | Bits | Bits | uint16 |  |  | Number of data bits per character |  | M
10 | 10 | 1 | RW | Pty | Parity | enum16 |  |  | Bitmask value. Parity setting |  | M
11 | 11 | 1 | RW | Dup | Duplex | enum16 |  |  | Enumerated value. Duplex mode |  | O
12 | 12 | 1 | RW | Flw | Flow Control | enum16 |  |  | Flow Control Method |  | O
13 | 13 | 1 | R | Typ | Interface Type | enum16 |  |  | Enumerated value. Interface type |  | O
14 | 14 | 1 | R | Pcol | Protocol | enum16 |  |  | Enumerated value. Serial protocol selection |  | O
// Pty enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NONE |  |  | 0 |  | none |  | No Parity
ODD |  |  | 1 |  | odd |  | Odd Parity
EVEN |  |  | 2 |  | even |  | Even Parity
// Dup enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
FULL |  |  | 0 |  | full |  | Full Duplex
HALF |  |  | 1 |  | half |  | Half Duplex
// Flw enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NONE |  |  | 0 |  | none |  | No flow control
HW |  |  | 1 |  | hardware |  | Hardware flow control
XONXOFF |  |  | 2 |  | software |  | Soft (XON/XOFF) flow control
// Typ enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
UNKNOWN |  |  | 0 |  | unknown |  | Unknown interface type
RS232 |  |  | 1 |  | RS232 |  | RS232 interface type
RS485 |  |  | 2 |  | RS485 |  | RS485 interface type
// Pcol enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
UNKNOWN |  |  | 0 |  | unknown |  | Unknown protocol
MODBUS |  |  | 1 |  | Modbus |  | Modbus protocol
VENDOR |  |  | 2 |  | vendor specific

## NC 018
// 18-Cellular Link : Include this model to support a cellular interface link ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 18. Uniquely identifies this as a SunSpec Cellular Link Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 22 |  | M
// 18 Cellular Link Fixed Block (22)
3 | 6 | 4 | RW | Nam | Name | string |  |  | Interface name |  | O
7 | 8 | 2 | RW | IMEI | IMEI | uint32 |  |  | International Mobile Equipment Identifier for the interface |  | O
9 | 12 | 4 | RW | APN | APN | string |  |  | Access Point Name for the interface |  | O
13 | 18 | 6 | RW | Num | Number | string |  |  | Phone number for the interface |  | O
19 | 24 | 6 | RW | Pin | PIN | string |  |  | Personal Identification Number for the interface |  | O

## NC 019
// 19-PPP Link : Include this model to configure a Point-to-Point Protocol link ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 19. Uniquely identifies this as a SunSpec PPP Link Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 30 |  | M
// 19 PPP Link Fixed Block (30)
3 | 6 | 4 | RW | Nam | Name | string |  |  | Interface name |  | O
7 | 8 | 2 | RW | Rte | Rate | uint32 | bps |  | Interface baud rate in bits per second |  | M
9 | 9 | 1 | RW | Bits | Bits | uint16 |  |  | Number of data bits per character |  | M
10 | 10 | 1 | RW | Pty | Parity | enum16 |  |  | Bitmask value. Parity setting |  | M
11 | 11 | 1 | RW | Dup | Duplex | enum16 |  |  | Enumerated value. Duplex mode |  | O
12 | 12 | 1 | RW | Flw | Flow Control | enum16 |  |  | Flow Control Method |  | O
13 | 13 | 1 | R | Auth | Authentication | enum16 |  |  | Enumerated value. Authentication method |  | O
14 | 25 | 12 | R | UsrNam | Username | string |  |  | Username for authentication |  | O
26 | 31 | 6 | R | Pw | Password | string |  |  | Password for authentication |  | O
32 | 32 | 1 | R | Pad |  | pad |  |  |  |  | O
// Pty enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NONE |  |  | 0 |  | none |  | No Parity
ODD |  |  | 1 |  | odd |  | Odd Parity
EVEN |  |  | 2 |  | even |  | Even Parity
// Dup enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
FULL |  |  | 0 |  | full |  | Full Duplex
HALF |  |  | 1 |  | half |  | Half Duplex
// Flw enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NONE |  |  | 0 |  | none |  | No flow control
HW |  |  | 1 |  | hardware |  | Hardware flow control
XONXOFF |  |  | 2 |  | software |  | Soft (XON/XOFF) flow control
// Auth enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NONE |  |  | 0 |  | none |  | No Authentication
PAP |  |  | 1 |  | PAP |  | Use PAP authentication
CHAP |  |  | 2 |  | CHAP |  | Use CHAP authentication

## I 101
// 101-Inverter (Single Phase) : Include this model for single phase inverter monitoring ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 101. Uniquely identifies this as a SunSpec Inverter (Single Phase) Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 50 |  | M
// 101 Inverter (Single Phase) Fixed Block (50)
3 | 3 | 1 | R | A | Amps | uint16 | A | A_SF | AC Current |  | M
4 | 4 | 1 | R | AphA | Amps PhaseA | uint16 | A | A_SF | Phase A Current | Connected Phase | M
5 | 5 | 1 | R | AphB | Amps PhaseB | uint16 | A | A_SF | Phase B Current |  | O
6 | 6 | 1 | R | AphC | Amps PhaseC | uint16 | A | A_SF | Phase C Current |  | O
7 | 7 | 1 | R | A_SF |  | sunssf |  |  |  |  | M
8 | 8 | 1 | R | PPVphAB | Phase Voltage AB | uint16 | V | V_SF | Phase Voltage AB |  | O
9 | 9 | 1 | R | PPVphBC | Phase Voltage BC | uint16 | V | V_SF | Phase Voltage BC |  | O
10 | 10 | 1 | R | PPVphCA | Phase Voltage CA | uint16 | V | V_SF | Phase Voltage CA |  | O
11 | 11 | 1 | R | PhVphA | Phase Voltage AN | uint16 | V | V_SF | Phase Voltage AN |  | M
12 | 12 | 1 | R | PhVphB | Phase Voltage BN | uint16 | V | V_SF | Phase Voltage BN |  | O
13 | 13 | 1 | R | PhVphC | Phase Voltage CN | uint16 | V | V_SF | Phase Voltage CN |  | O
14 | 14 | 1 | R | V_SF |  | sunssf |  |  |  |  | M
15 | 15 | 1 | R | W | Watts | int16 | W | W_SF | AC Power |  | M
16 | 16 | 1 | R | W_SF |  | sunssf |  |  |  |  | M
17 | 17 | 1 | R | Hz | Hz | uint16 | Hz | Hz_SF | Line Frequency |  | M
18 | 18 | 1 | R | Hz_SF |  | sunssf |  |  |  |  | M
19 | 19 | 1 | R | VA | VA | int16 | VA | VA_SF | AC Apparent Power |  | O
20 | 20 | 1 | R | VA_SF |  | sunssf |  |  |  |  | O
21 | 21 | 1 | R | VAr | VAr | int16 | var | VAr_SF | AC Reactive Power |  | O
22 | 22 | 1 | R | VAr_SF |  | sunssf |  |  |  |  | O
23 | 23 | 1 | R | PF | PF | int16 | Pct | PF_SF | AC Power Factor |  | O
24 | 24 | 1 | R | PF_SF |  | sunssf |  |  |  |  | O
25 | 26 | 2 | R | WH | WattHours | acc32 | Wh | WH_SF | AC Energy |  | M
27 | 27 | 1 | R | WH_SF |  | sunssf |  |  |  |  | M
28 | 28 | 1 | R | DCA | DC Amps | uint16 | A | DCA_SF | DC Current |  | O
29 | 29 | 1 | R | DCA_SF |  | sunssf |  |  |  |  | O
30 | 30 | 1 | R | DCV | DC Voltage | uint16 | V | DCV_SF | DC Voltage |  | O
31 | 31 | 1 | R | DCV_SF |  | sunssf |  |  |  |  | O
32 | 32 | 1 | R | DCW | DC Watts | int16 | W | DCW_SF | DC Power |  | O
33 | 33 | 1 | R | DCW_SF |  | sunssf |  |  |  |  | O
34 | 34 | 1 | R | TmpCab | Cabinet Temperature | int16 | C | Tmp_SF | Cabinet Temperature |  | M
35 | 35 | 1 | R | TmpSnk | Heat Sink Temperature | int16 | C | Tmp_SF | Heat Sink Temperature |  | O
36 | 36 | 1 | R | TmpTrns | Transformer Temperature | int16 | C | Tmp_SF | Transformer Temperature |  | O
37 | 37 | 1 | R | TmpOt | Other Temperature | int16 | C | Tmp_SF | Other Temperature |  | O
38 | 38 | 1 | R | Tmp_SF |  | sunssf |  |  |  |  | M
39 | 39 | 1 | R | St | Operating State | enum16 |  |  | Enumerated value. Operating state |  | M
40 | 40 | 1 | R | StVnd | Vendor Operating State | enum16 |  |  | Vendor specific operating state code |  | O
41 | 42 | 2 | R | Evt1 | Event1 | bitfield32 |  |  | Bitmask value. Event fields |  | M
43 | 44 | 2 | R | Evt2 | Event Bitfield 2 | bitfield32 |  |  | Reserved for future use |  | M
45 | 46 | 2 | R | EvtVnd1 | Vendor Event Bitfield 1 | bitfield32 |  |  | Vendor defined events |  | O
47 | 48 | 2 | R | EvtVnd2 | Vendor Event Bitfield 2 | bitfield32 |  |  | Vendor defined events |  | O
49 | 50 | 2 | R | EvtVnd3 | Vendor Event Bitfield 3 | bitfield32 |  |  | Vendor defined events |  | O
51 | 52 | 2 | R | EvtVnd4 | Vendor Event Bitfield 4 | bitfield32 |  |  | Vendor defined events |  | O
// St enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
OFF |  |  | 1 |  | Off |  | Device is not operating
SLEEPING |  |  | 2 |  | Sleeping |  | Device is sleeping / auto-shudown
STARTING |  |  | 3 |  | Starting |  | Device is staring up
MPPT |  |  | 4 |  | MPPT |  | Device is auto tracking maximum power point
THROTTLED |  |  | 5 |  | Throttled |  | Device is operating at reduced power output
SHUTTING_DOWN |  |  | 6 |  | Shutting down |  | Device is shutting down
FAULT |  |  | 7 |  | Fault |  | One or more faults exist
STANDBY |  |  | 8 |  | Standby |  | Device is in standby mode
// Evt1 bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
GROUND_FAULT |  |  | 0 |  | Ground fault
DC_OVER_VOLT |  |  | 1 |  | DC over voltage
AC_DISCONNECT |  |  | 2 |  | AC disconnect open
DC_DISCONNECT |  |  | 3 |  | DC disconnect open
GRID_DISCONNECT |  |  | 4 |  | Grid disconnect
CABINET_OPEN |  |  | 5 |  | Cabinet open
MANUAL_SHUTDOWN |  |  | 6 |  | Manual shutdown
OVER_TEMP |  |  | 7 |  | Over temperature
OVER_FREQUENCY |  |  | 8 |  | Frequency above limit
UNDER_FREQUENCY |  |  | 9 |  | Frequency under limit
AC_OVER_VOLT |  |  | 10 |  | AC Voltage above limit
AC_UNDER_VOLT |  |  | 11 |  | AC Voltage under limit
BLOWN_STRING_FUSE |  |  | 12 |  | Blown String fuse on input
UNDER_TEMP |  |  | 13 |  | Under temperature
MEMORY_LOSS |  |  | 14 |  | Generic Memory or Communication error (internal)
HW_TEST_FAILURE |  |  | 15 |  | Hardware test failure

## I 102
// 102-Inverter (Split-Phase) : Include this model for split phase inverter monitoring ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 102. Uniquely identifies this as a SunSpec Inverter (Split-Phase) Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 50 |  | M
// 102 Inverter (Split-Phase) Fixed Block (50)
3 | 3 | 1 | R | A | Amps | uint16 | A | A_SF | AC Current | Sum of active phases | M
4 | 4 | 1 | R | AphA | Amps PhaseA | uint16 | A | A_SF | Phase A Current | Connected Phase | M
5 | 5 | 1 | R | AphB | Amps PhaseB | uint16 | A | A_SF | Phase B Current | Connected Phase | M
6 | 6 | 1 | R | AphC | Amps PhaseC | uint16 | A | A_SF | Phase C Current |  | O
7 | 7 | 1 | R | A_SF |  | sunssf |  |  |  |  | M
8 | 8 | 1 | R | PPVphAB | Phase Voltage AB | uint16 | V | V_SF | Phase Voltage AB |  | O
9 | 9 | 1 | R | PPVphBC | Phase Voltage BC | uint16 | V | V_SF | Phase Voltage BC |  | O
10 | 10 | 1 | R | PPVphCA | Phase Voltage CA | uint16 | V | V_SF | Phase Voltage CA |  | O
11 | 11 | 1 | R | PhVphA | Phase Voltage AN | uint16 | V | V_SF | Phase Voltage AN |  | M
12 | 12 | 1 | R | PhVphB | Phase Voltage BN | uint16 | V | V_SF | Phase Voltage BN |  | M
13 | 13 | 1 | R | PhVphC | Phase Voltage CN | uint16 | V | V_SF | Phase Voltage CN |  | O
14 | 14 | 1 | R | V_SF |  | sunssf |  |  |  |  | M
15 | 15 | 1 | R | W | Watts | int16 | W | W_SF | AC Power |  | M
16 | 16 | 1 | R | W_SF |  | sunssf |  |  |  |  | M
17 | 17 | 1 | R | Hz | Hz | uint16 | Hz | Hz_SF | Line Frequency |  | M
18 | 18 | 1 | R | Hz_SF |  | sunssf |  |  |  |  | M
19 | 19 | 1 | R | VA | VA | int16 | VA | VA_SF | AC Apparent Power |  | O
20 | 20 | 1 | R | VA_SF |  | sunssf |  |  |  |  | O
21 | 21 | 1 | R | VAr | VAr | int16 | var | VAr_SF | AC Reactive Power |  | O
22 | 22 | 1 | R | VAr_SF |  | sunssf |  |  |  |  | O
23 | 23 | 1 | R | PF | PF | int16 | Pct | PF_SF | AC Power Factor |  | O
24 | 24 | 1 | R | PF_SF |  | sunssf |  |  |  |  | O
25 | 26 | 2 | R | WH | WattHours | acc32 | Wh | WH_SF | AC Energy |  | M
27 | 27 | 1 | R | WH_SF |  | sunssf |  |  |  |  | M
28 | 28 | 1 | R | DCA | DC Amps | uint16 | A | DCA_SF | DC Current |  | O
29 | 29 | 1 | R | DCA_SF |  | sunssf |  |  |  |  | O
30 | 30 | 1 | R | DCV | DC Voltage | uint16 | V | DCV_SF | DC Voltage |  | O
31 | 31 | 1 | R | DCV_SF |  | sunssf |  |  |  |  | O
32 | 32 | 1 | R | DCW | DC Watts | int16 | W | DCW_SF | DC Power |  | O
33 | 33 | 1 | R | DCW_SF |  | sunssf |  |  |  |  | O
34 | 34 | 1 | R | TmpCab | Cabinet Temperature | int16 | C | Tmp_SF | Cabinet Temperature |  | M
35 | 35 | 1 | R | TmpSnk | Heat Sink Temperature | int16 | C | Tmp_SF | Heat Sink Temperature |  | O
36 | 36 | 1 | R | TmpTrns | Transformer Temperature | int16 | C | Tmp_SF | Transformer Temperature |  | O
37 | 37 | 1 | R | TmpOt | Other Temperature | int16 | C | Tmp_SF | Other Temperature |  | O
38 | 38 | 1 | R | Tmp_SF |  | sunssf |  |  |  |  | M
39 | 39 | 1 | R | St | Operating State | enum16 |  |  | Enumerated value. Operating state |  | M
40 | 40 | 1 | R | StVnd | Vendor Operating State | enum16 |  |  | Vendor specific operating state code |  | O
41 | 42 | 2 | R | Evt1 | Event1 | bitfield32 |  |  | Bitmask value. Event fields |  | M
43 | 44 | 2 | R | Evt2 | Event Bitfield 2 | bitfield32 |  |  | Reserved for future use |  | M
45 | 46 | 2 | R | EvtVnd1 | Vendor Event Bitfield 1 | bitfield32 |  |  | Vendor defined events |  | O
47 | 48 | 2 | R | EvtVnd2 | Vendor Event Bitfield 2 | bitfield32 |  |  | Vendor defined events |  | O
49 | 50 | 2 | R | EvtVnd3 | Vendor Event Bitfield 3 | bitfield32 |  |  | Vendor defined events |  | O
51 | 52 | 2 | R | EvtVnd4 | Vendor Event Bitfield 4 | bitfield32 |  |  | Vendor defined events |  | O
// St enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
OFF |  |  | 1 |  | Off |  | Device is not operating
SLEEPING |  |  | 2 |  | Sleeping |  | Device is sleeping / auto-shudown
STARTING |  |  | 3 |  | Starting |  | Device is staring up
MPPT |  |  | 4 |  | MPPT |  | Device is auto tracking maximum power point
THROTTLED |  |  | 5 |  | Throttled |  | Device is operating at reduced power output
SHUTTING_DOWN |  |  | 6 |  | Shutting down |  | Device is shutting down
FAULT |  |  | 7 |  | Fault |  | One or more faults exist
STANDBY |  |  | 8 |  | Standby |  | Device is in standby mode
// Evt1 bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
GROUND_FAULT |  |  | 0 |  | Ground fault
DC_OVER_VOLT |  |  | 1 |  | DC over voltage
AC_DISCONNECT |  |  | 2 |  | AC disconnect open
DC_DISCONNECT |  |  | 3 |  | DC disconnect open
GRID_DISCONNECT |  |  | 4 |  | Grid shutdown
CABINET_OPEN |  |  | 5 |  | Cabinet open
MANUAL_SHUTDOWN |  |  | 6 |  | Manual shutdown
OVER_TEMP |  |  | 7 |  | Over temperature
OVER_FREQUENCY |  |  | 8 |  | Frequency above limit
UNDER_FREQUENCY |  |  | 9 |  | Frequency under limit
AC_OVER_VOLT |  |  | 10 |  | AC Voltage above limit
AC_UNDER_VOLT |  |  | 11 |  | AC Voltage under limit
BLOWN_STRING_FUSE |  |  | 12 |  | Blown String fuse on input
UNDER_TEMP |  |  | 13 |  | Under temperature
MEMORY_LOSS |  |  | 14 |  | Generic Memory or Communication error (internal)
HW_TEST_FAILURE |  |  | 15 |  | Hardware test failure

## I 103
// 103-Inverter (Three Phase) : Include this model for three phase inverter monitoring ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 103. Uniquely identifies this as a SunSpec Inverter (Three Phase) Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 50 |  | M
// 103 Inverter (Three Phase) Fixed Block (50)
3 | 3 | 1 | R | A | Amps | uint16 | A | A_SF | AC Current | Sum of active phases | M
4 | 4 | 1 | R | AphA | Amps PhaseA | uint16 | A | A_SF | Phase A Current | Connected Phase | M
5 | 5 | 1 | R | AphB | Amps PhaseB | uint16 | A | A_SF | Phase B Current | Connected Phase | M
6 | 6 | 1 | R | AphC | Amps PhaseC | uint16 | A | A_SF | Phase C Current | Connected Phase | M
7 | 7 | 1 | R | A_SF |  | sunssf |  |  |  |  | M
8 | 8 | 1 | R | PPVphAB | Phase Voltage AB | uint16 | V | V_SF | Phase Voltage AB |  | O
9 | 9 | 1 | R | PPVphBC | Phase Voltage BC | uint16 | V | V_SF | Phase Voltage BC |  | O
10 | 10 | 1 | R | PPVphCA | Phase Voltage CA | uint16 | V | V_SF | Phase Voltage CA |  | O
11 | 11 | 1 | R | PhVphA | Phase Voltage AN | uint16 | V | V_SF | Phase Voltage AN |  | M
12 | 12 | 1 | R | PhVphB | Phase Voltage BN | uint16 | V | V_SF | Phase Voltage BN |  | M
13 | 13 | 1 | R | PhVphC | Phase Voltage CN | uint16 | V | V_SF | Phase Voltage CN |  | M
14 | 14 | 1 | R | V_SF |  | sunssf |  |  |  |  | M
15 | 15 | 1 | R | W | Watts | int16 | W | W_SF | AC Power |  | M
16 | 16 | 1 | R | W_SF |  | sunssf |  |  |  |  | M
17 | 17 | 1 | R | Hz | Hz | uint16 | Hz | Hz_SF | Line Frequency |  | M
18 | 18 | 1 | R | Hz_SF |  | sunssf |  |  |  |  | M
19 | 19 | 1 | R | VA | VA | int16 | VA | VA_SF | AC Apparent Power |  | O
20 | 20 | 1 | R | VA_SF |  | sunssf |  |  |  |  | O
21 | 21 | 1 | R | VAr | VAr | int16 | var | VAr_SF | AC Reactive Power |  | O
22 | 22 | 1 | R | VAr_SF |  | sunssf |  |  |  |  | O
23 | 23 | 1 | R | PF | PF | int16 | Pct | PF_SF | AC Power Factor |  | O
24 | 24 | 1 | R | PF_SF |  | sunssf |  |  |  |  | O
25 | 26 | 2 | R | WH | WattHours | acc32 | Wh | WH_SF | AC Energy |  | M
27 | 27 | 1 | R | WH_SF |  | sunssf |  |  |  |  | M
28 | 28 | 1 | R | DCA | DC Amps | uint16 | A | DCA_SF | DC Current |  | O
29 | 29 | 1 | R | DCA_SF |  | sunssf |  |  |  |  | O
30 | 30 | 1 | R | DCV | DC Voltage | uint16 | V | DCV_SF | DC Voltage |  | O
31 | 31 | 1 | R | DCV_SF |  | sunssf |  |  |  |  | O
32 | 32 | 1 | R | DCW | DC Watts | int16 | W | DCW_SF | DC Power |  | O
33 | 33 | 1 | R | DCW_SF |  | sunssf |  |  |  |  | O
34 | 34 | 1 | R | TmpCab | Cabinet Temperature | int16 | C | Tmp_SF | Cabinet Temperature |  | M
35 | 35 | 1 | R | TmpSnk | Heat Sink Temperature | int16 | C | Tmp_SF | Heat Sink Temperature |  | O
36 | 36 | 1 | R | TmpTrns | Transformer Temperature | int16 | C | Tmp_SF | Transformer Temperature |  | O
37 | 37 | 1 | R | TmpOt | Other Temperature | int16 | C | Tmp_SF | Other Temperature |  | O
38 | 38 | 1 | R | Tmp_SF |  | sunssf |  |  |  |  | M
39 | 39 | 1 | R | St | Operating State | enum16 |  |  | Enumerated value. Operating state |  | M
40 | 40 | 1 | R | StVnd | Vendor Operating State | enum16 |  |  | Vendor specific operating state code |  | O
41 | 42 | 2 | R | Evt1 | Event1 | bitfield32 |  |  | Bitmask value. Event fields |  | M
43 | 44 | 2 | R | Evt2 | Event Bitfield 2 | bitfield32 |  |  | Reserved for future use |  | M
45 | 46 | 2 | R | EvtVnd1 | Vendor Event Bitfield 1 | bitfield32 |  |  | Vendor defined events |  | O
47 | 48 | 2 | R | EvtVnd2 | Vendor Event Bitfield 2 | bitfield32 |  |  | Vendor defined events |  | O
49 | 50 | 2 | R | EvtVnd3 | Vendor Event Bitfield 3 | bitfield32 |  |  | Vendor defined events |  | O
51 | 52 | 2 | R | EvtVnd4 | Vendor Event Bitfield 4 | bitfield32 |  |  | Vendor defined events |  | O
// St enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
OFF |  |  | 1 |  | Off |  | Device is not operating
SLEEPING |  |  | 2 |  | Sleeping |  | Device is sleeping / auto-shudown
STARTING |  |  | 3 |  | Starting |  | Device is staring up
MPPT |  |  | 4 |  | MPPT |  | Device is auto tracking maximum power point
THROTTLED |  |  | 5 |  | Throttled |  | Device is operating at reduced power output
SHUTTING_DOWN |  |  | 6 |  | Shutting down |  | Device is shutting down
FAULT |  |  | 7 |  | Fault |  | One or more faults exist
STANDBY |  |  | 8 |  | Standby |  | Device is in standby mode
// Evt1 bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
GROUND_FAULT |  |  | 0 |  | Ground fault
DC_OVER_VOLT |  |  | 1 |  | DC over voltage
AC_DISCONNECT |  |  | 2 |  | AC disconnect open
DC_DISCONNECT |  |  | 3 |  | DC disconnect open
GRID_DISCONNECT |  |  | 4 |  | Grid shutdown
CABINET_OPEN |  |  | 5 |  | Cabinet open
MANUAL_SHUTDOWN |  |  | 6 |  | Manual shutdown
OVER_TEMP |  |  | 7 |  | Over temperature
OVER_FREQUENCY |  |  | 8 |  | Frequency above limit
UNDER_FREQUENCY |  |  | 9 |  | Frequency under limit
AC_OVER_VOLT |  |  | 10 |  | AC Voltage above limit
AC_UNDER_VOLT |  |  | 11 |  | AC Voltage under limit
BLOWN_STRING_FUSE |  |  | 12 |  | Blown String fuse on input
UNDER_TEMP |  |  | 13 |  | Under temperature
MEMORY_LOSS |  |  | 14 |  | Generic Memory or Communication error (internal)
HW_TEST_FAILURE |  |  | 15 |  | Hardware test failure

## I 111
// 111-Inverter (Single Phase) FLOAT : Include this model for single phase inverter monitoring using float values ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 111. Uniquely identifies this as a SunSpec Inverter (Single Phase) FLOAT Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 60 |  | M
// 111 Inverter (Single Phase) FLOAT Fixed Block (60)
3 | 4 | 2 | R | A | Amps | float32 | A |  | AC Current |  | M
5 | 6 | 2 | R | AphA | Amps PhaseA | float32 | A |  | Phase A Current | Connected Phase | M
7 | 8 | 2 | R | AphB | Amps PhaseB | float32 | A |  | Phase B Current |  | O
9 | 10 | 2 | R | AphC | Amps PhaseC | float32 | A |  | Phase C Current |  | O
11 | 12 | 2 | R | PPVphAB | Phase Voltage AB | float32 | V |  | Phase Voltage AB |  | O
13 | 14 | 2 | R | PPVphBC | Phase Voltage BC | float32 | V |  | Phase Voltage BC |  | O
15 | 16 | 2 | R | PPVphCA | Phase Voltage CA | float32 | V |  | Phase Voltage CA |  | O
17 | 18 | 2 | R | PhVphA | Phase Voltage AN | float32 | V |  | Phase Voltage AN |  | M
19 | 20 | 2 | R | PhVphB | Phase Voltage BN | float32 | V |  | Phase Voltage BN |  | O
21 | 22 | 2 | R | PhVphC | Phase Voltage CN | float32 | V |  | Phase Voltage CN |  | O
23 | 24 | 2 | R | W | Watts | float32 | W |  | AC Power |  | M
25 | 26 | 2 | R | Hz | Hz | float32 | Hz |  | Line Frequency |  | M
27 | 28 | 2 | R | VA | VA | float32 | VA |  | AC Apparent Power |  | O
29 | 30 | 2 | R | VAr | VAr | float32 | var |  | AC Reactive Power |  | O
31 | 32 | 2 | R | PF | PF | float32 | Pct |  | AC Power Factor |  | O
33 | 34 | 2 | R | WH | WattHours | float32 | Wh |  | AC Energy |  | M
35 | 36 | 2 | R | DCA | DC Amps | float32 | A |  | DC Current |  | O
37 | 38 | 2 | R | DCV | DC Voltage | float32 | V |  | DC Voltage |  | O
39 | 40 | 2 | R | DCW | DC Watts | float32 | W |  | DC Power |  | O
41 | 42 | 2 | R | TmpCab | Cabinet Temperature | float32 | C |  | Cabinet Temperature |  | M
43 | 44 | 2 | R | TmpSnk | Heat Sink Temperature | float32 | C |  | Heat Sink Temperature |  | O
45 | 46 | 2 | R | TmpTrns | Transformer Temperature | float32 | C |  | Transformer Temperature |  | O
47 | 48 | 2 | R | TmpOt | Other Temperature | float32 | C |  | Other Temperature |  | O
49 | 49 | 1 | R | St | Operating State | enum16 |  |  | Enumerated value. Operating state |  | M
50 | 50 | 1 | R | StVnd | Vendor Operating State | enum16 |  |  | Vendor specific operating state code |  | O
51 | 52 | 2 | R | Evt1 | Event1 | bitfield32 |  |  | Bitmask value. Event fields |  | M
53 | 54 | 2 | R | Evt2 | Event Bitfield 2 | bitfield32 |  |  | Reserved for future use |  | M
55 | 56 | 2 | R | EvtVnd1 | Vendor Event Bitfield 1 | bitfield32 |  |  | Vendor defined events |  | O
57 | 58 | 2 | R | EvtVnd2 | Vendor Event Bitfield 2 | bitfield32 |  |  | Vendor defined events |  | O
59 | 60 | 2 | R | EvtVnd3 | Vendor Event Bitfield 3 | bitfield32 |  |  | Vendor defined events |  | O
61 | 62 | 2 | R | EvtVnd4 | Vendor Event Bitfield 4 | bitfield32 |  |  | Vendor defined events |  | O
// St enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ggOFF |  |  | 1
ggSLEEPING |  |  | 2
ggSTARTING |  |  | 3
ggMPPT |  |  | 4 |  | MPPT |  | Device is auto tracking maximum power point
ggTHROTTLED |  |  | 5
ggSHUTTING_DOWN |  |  | 6
ggFAULT |  |  | 7
ggSTANDBY |  |  | 8
// Evt1 bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
GROUND_FAULT |  |  | 0 |  | Ground fault
DC_OVER_VOLT |  |  | 1 |  | DC over voltage
AC_DISCONNECT |  |  | 2 |  | AC disconnect open
DC_DISCONNECT |  |  | 3 |  | DC disconnect open
GRID_DISCONNECT |  |  | 4 |  | Grid shutdown
CABINET_OPEN |  |  | 5 |  | Cabinet open
MANUAL_SHUTDOWN |  |  | 6 |  | Manual shutdown
OVER_TEMP |  |  | 7 |  | Over temperature
OVER_FREQUENCY |  |  | 8 |  | Frequency above limit
UNDER_FREQUENCY |  |  | 9 |  | Frequency under limit
AC_OVER_VOLT |  |  | 10 |  | AC Voltage above limit
AC_UNDER_VOLT |  |  | 11 |  | AC Voltage under limit
BLOWN_STRING_FUSE |  |  | 12 |  | Blown String fuse on input
UNDER_TEMP |  |  | 13 |  | Under temperature
MEMORY_LOSS |  |  | 14 |  | Generic Memory or Communication error (internal)
HW_TEST_FAILURE |  |  | 15 |  | Hardware test failure

## I 112
// 112-Inverter (Split Phase) FLOAT : Include this model for split phase inverter monitoring using float values ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 112. Uniquely identifies this as a SunSpec Inverter (Split Phase) FLOAT Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 60 |  | M
// 112 Inverter (Split Phase) FLOAT Fixed Block (60)
3 | 4 | 2 | R | A | Amps | float32 | A |  | AC Current |  | M
5 | 6 | 2 | R | AphA | Amps PhaseA | float32 | A |  | Phase A Current | Connected Phase | M
7 | 8 | 2 | R | AphB | Amps PhaseB | float32 | A |  | Phase B Current | Connected Phase | M
9 | 10 | 2 | R | AphC | Amps PhaseC | float32 | A |  | Phase C Current |  | O
11 | 12 | 2 | R | PPVphAB | Phase Voltage AB | float32 | V |  | Phase Voltage AB |  | O
13 | 14 | 2 | R | PPVphBC | Phase Voltage BC | float32 | V |  | Phase Voltage BC |  | O
15 | 16 | 2 | R | PPVphCA | Phase Voltage CA | float32 | V |  | Phase Voltage CA |  | O
17 | 18 | 2 | R | PhVphA | Phase Voltage AN | float32 | V |  | Phase Voltage AN |  | M
19 | 20 | 2 | R | PhVphB | Phase Voltage BN | float32 | V |  | Phase Voltage BN |  | M
21 | 22 | 2 | R | PhVphC | Phase Voltage CN | float32 | V |  | Phase Voltage CN |  | O
23 | 24 | 2 | R | W | Watts | float32 | W |  | AC Power |  | M
25 | 26 | 2 | R | Hz | Hz | float32 | Hz |  | Line Frequency |  | M
27 | 28 | 2 | R | VA | VA | float32 | VA |  | AC Apparent Power |  | O
29 | 30 | 2 | R | VAr | VAr | float32 | var |  | AC Reactive Power |  | O
31 | 32 | 2 | R | PF | PF | float32 | Pct |  | AC Power Factor |  | O
33 | 34 | 2 | R | WH | WattHours | float32 | Wh |  | AC Energy |  | M
35 | 36 | 2 | R | DCA | DC Amps | float32 | A |  | DC Current |  | O
37 | 38 | 2 | R | DCV | DC Voltage | float32 | V |  | DC Voltage |  | O
39 | 40 | 2 | R | DCW | DC Watts | float32 | W |  | DC Power |  | O
41 | 42 | 2 | R | TmpCab | Cabinet Temperature | float32 | C |  | Cabinet Temperature |  | M
43 | 44 | 2 | R | TmpSnk | Heat Sink Temperature | float32 | C |  | Heat Sink Temperature |  | O
45 | 46 | 2 | R | TmpTrns | Transformer Temperature | float32 | C |  | Transformer Temperature |  | O
47 | 48 | 2 | R | TmpOt | Other Temperature | float32 | C |  | Other Temperature |  | O
49 | 49 | 1 | R | St | Operating State | enum16 |  |  | Enumerated value. Operating state |  | M
50 | 50 | 1 | R | StVnd | Vendor Operating State | enum16 |  |  | Vendor specific operating state code |  | O
51 | 52 | 2 | R | Evt1 | Event1 | bitfield32 |  |  | Bitmask value. Event fields |  | M
53 | 54 | 2 | R | Evt2 | Event Bitfield 2 | bitfield32 |  |  | Reserved for future use |  | M
55 | 56 | 2 | R | EvtVnd1 | Vendor Event Bitfield 1 | bitfield32 |  |  | Vendor defined events |  | O
57 | 58 | 2 | R | EvtVnd2 | Vendor Event Bitfield 2 | bitfield32 |  |  | Vendor defined events |  | O
59 | 60 | 2 | R | EvtVnd3 | Vendor Event Bitfield 3 | bitfield32 |  |  | Vendor defined events |  | O
61 | 62 | 2 | R | EvtVnd4 | Vendor Event Bitfield 4 | bitfield32 |  |  | Vendor defined events |  | O
// St enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
OFF |  |  | 1 |  | Off |  | Device is not operating
SLEEPING |  |  | 2 |  | Sleeping |  | Device is sleeping / auto-shudown
STARTING |  |  | 3 |  | Starting |  | Device is staring up
MPPT |  |  | 4 |  | MPPT |  | Device is auto tracking maximum power point
THROTTLED |  |  | 5 |  | Throttled |  | Device is operating at reduced power output
SHUTTING_DOWN |  |  | 6 |  | Shutting down |  | Device is shutting down
FAULT |  |  | 7 |  | Fault |  | One or more faults exist
STANDBY |  |  | 8 |  | Standby |  | Device is in standby mode
// Evt1 bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
GROUND_FAULT |  |  | 0 |  | Ground fault
DC_OVER_VOLT |  |  | 1 |  | DC over voltage
AC_DISCONNECT |  |  | 2 |  | AC disconnect open
DC_DISCONNECT |  |  | 3 |  | DC disconnect open
GRID_DISCONNECT |  |  | 4 |  | Grid shutdown
CABINET_OPEN |  |  | 5 |  | Cabinet open
MANUAL_SHUTDOWN |  |  | 6 |  | Manual shutdown
OVER_TEMP |  |  | 7 |  | Over temperature
OVER_FREQUENCY |  |  | 8 |  | Frequency above limit
UNDER_FREQUENCY |  |  | 9 |  | Frequency under limit
AC_OVER_VOLT |  |  | 10 |  | AC Voltage above limit
AC_UNDER_VOLT |  |  | 11 |  | AC Voltage under limit
BLOWN_STRING_FUSE |  |  | 12 |  | Blown String fuse on input
UNDER_TEMP |  |  | 13 |  | Under temperature
MEMORY_LOSS |  |  | 14 |  | Generic Memory or Communication error (internal)
HW_TEST_FAILURE |  |  | 15 |  | Hardware test failure

## I 113
// 113-Inverter (Three Phase) FLOAT : Include this model for three phase inverter monitoring using float values ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 113. Uniquely identifies this as a SunSpec Inverter (Three Phase) FLOAT Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 60 |  | M
// 113 Inverter (Three Phase) FLOAT Fixed Block (60)
3 | 4 | 2 | R | A | Amps | float32 | A |  | AC Current | Sum of active phases | M
5 | 6 | 2 | R | AphA | Amps PhaseA | float32 | A |  | Phase A Current | Connected Phase | M
7 | 8 | 2 | R | AphB | Amps PhaseB | float32 | A |  | Phase B Current | Connected Phase | M
9 | 10 | 2 | R | AphC | Amps PhaseC | float32 | A |  | Phase C Current | Connected Phase | M
11 | 12 | 2 | R | PPVphAB | Phase Voltage AB | float32 | V |  | Phase Voltage AB |  | O
13 | 14 | 2 | R | PPVphBC | Phase Voltage BC | float32 | V |  | Phase Voltage BC |  | O
15 | 16 | 2 | R | PPVphCA | Phase Voltage CA | float32 | V |  | Phase Voltage CA |  | O
17 | 18 | 2 | R | PhVphA | Phase Voltage AN | float32 | V |  | Phase Voltage AN |  | M
19 | 20 | 2 | R | PhVphB | Phase Voltage BN | float32 | V |  | Phase Voltage BN |  | M
21 | 22 | 2 | R | PhVphC | Phase Voltage CN | float32 | V |  | Phase Voltage CN |  | M
23 | 24 | 2 | R | W | Watts | float32 | W |  | AC Power |  | M
25 | 26 | 2 | R | Hz | Hz | float32 | Hz |  | Line Frequency |  | M
27 | 28 | 2 | R | VA | VA | float32 | VA |  | AC Apparent Power |  | O
29 | 30 | 2 | R | VAr | VAr | float32 | var |  | AC Reactive Power |  | O
31 | 32 | 2 | R | PF | PF | float32 | Pct |  | AC Power Factor |  | O
33 | 34 | 2 | R | WH | WattHours | float32 | Wh |  | AC Energy |  | M
35 | 36 | 2 | R | DCA | DC Amps | float32 | A |  | DC Current |  | O
37 | 38 | 2 | R | DCV | DC Voltage | float32 | V |  | DC Voltage |  | O
39 | 40 | 2 | R | DCW | DC Watts | float32 | W |  | DC Power |  | O
41 | 42 | 2 | R | TmpCab | Cabinet Temperature | float32 | C |  | Cabinet Temperature |  | M
43 | 44 | 2 | R | TmpSnk | Heat Sink Temperature | float32 | C |  | Heat Sink Temperature |  | O
45 | 46 | 2 | R | TmpTrns | Transformer Temperature | float32 | C |  | Transformer Temperature |  | O
47 | 48 | 2 | R | TmpOt | Other Temperature | float32 | C |  | Other Temperature |  | O
49 | 49 | 1 | R | St | Operating State | enum16 |  |  | Enumerated value. Operating state |  | M
50 | 50 | 1 | R | StVnd | Vendor Operating State | enum16 |  |  | Vendor specific operating state code |  | O
51 | 52 | 2 | R | Evt1 | Event1 | bitfield32 |  |  | Bitmask value. Event fields |  | M
53 | 54 | 2 | R | Evt2 | Event Bitfield 2 | bitfield32 |  |  | Reserved for future use |  | M
55 | 56 | 2 | R | EvtVnd1 | Vendor Event Bitfield 1 | bitfield32 |  |  | Vendor defined events |  | O
57 | 58 | 2 | R | EvtVnd2 | Vendor Event Bitfield 2 | bitfield32 |  |  | Vendor defined events |  | O
59 | 60 | 2 | R | EvtVnd3 | Vendor Event Bitfield 3 | bitfield32 |  |  | Vendor defined events |  | O
61 | 62 | 2 | R | EvtVnd4 | Vendor Event Bitfield 4 | bitfield32 |  |  | Vendor defined events |  | O
// St enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
OFF |  |  | 1 |  | Off |  | Device is not operating
SLEEPING |  |  | 2 |  | Sleeping |  | Device is sleeping / auto-shudown
STARTING |  |  | 3 |  | Starting |  | Device is staring up
MPPT |  |  | 4 |  | MPPT |  | Device is auto tracking maximum power point
THROTTLED |  |  | 5 |  | Throttled |  | Device is operating at reduced power output
SHUTTING_DOWN |  |  | 6 |  | Shutting down |  | Device is shutting down
FAULT |  |  | 7 |  | Fault |  | One or more faults exist
STANDBY |  |  | 8 |  | Standby |  | Device is in standby mode
// Evt1 bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
GROUND_FAULT |  |  | 0 |  | Ground fault
DC_OVER_VOLT |  |  | 1 |  | DC over voltage
AC_DISCONNECT |  |  | 2 |  | AC disconnect open
DC_DISCONNECT |  |  | 3 |  | DC disconnect open
GRID_DISCONNECT |  |  | 4 |  | Grid shutdown
CABINET_OPEN |  |  | 5 |  | Cabinet open
MANUAL_SHUTDOWN |  |  | 6 |  | Manual shutdown
OVER_TEMP |  |  | 7 |  | Over temperature
OVER_FREQUENCY |  |  | 8 |  | Frequency above limit
UNDER_FREQUENCY |  |  | 9 |  | Frequency under limit
AC_OVER_VOLT |  |  | 10 |  | AC Voltage above limit
AC_UNDER_VOLT |  |  | 11 |  | AC Voltage under limit
BLOWN_STRING_FUSE |  |  | 12 |  | Blown String fuse on input
UNDER_TEMP |  |  | 13 |  | Under temperature
MEMORY_LOSS |  |  | 14 |  | Generic Memory or Communication error (internal)
HW_TEST_FAILURE |  |  | 15 |  | Hardware test failure

## IC 120
// 120-Nameplate : Inverter Controls Nameplate Ratings (Ref 3: 8.14.3.2, Ref 4: 17)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 26 |  | M
// 120 Nameplate Fixed Block (26)
3 | 3 | 1 | R | DERTyp | DERTyp | enum16 |  |  | Type of DER device. Default value is 4 to indicate PV device. |  | M
4 | 4 | 1 | R | WRtg | WRtg | uint16 | W | WRtg_SF | Continuous power output capability of the inverter. |  | M
5 | 5 | 1 | R | WRtg_SF | WRtg_SF | sunssf |  |  | Scale factor |  | M
6 | 6 | 1 | R | VARtg | VARtg | uint16 | VA | VARtg_SF | Continuous Volt-Ampere capability of the inverter. |  | M
7 | 7 | 1 | R | VARtg_SF | VARtg_SF | sunssf |  |  | Scale factor |  | M
8 | 8 | 1 | R | VArRtgQ1 | VArRtgQ1 | int16 | var | VArRtg_SF | Continuous VAR capability of the inverter in quadrant 1. |  | M
9 | 9 | 1 | R | VArRtgQ2 | VArRtgQ2 | int16 | var | VArRtg_SF | Continuous VAR capability of the inverter in quadrant 2. |  | M
10 | 10 | 1 | R | VArRtgQ3 | VArRtgQ3 | int16 | var | VArRtg_SF | Continuous VAR capability of the inverter in quadrant 3. |  | M
11 | 11 | 1 | R | VArRtgQ4 | VArRtgQ4 | int16 | var | VArRtg_SF | Continuous VAR capability of the inverter in quadrant 4. |  | M
12 | 12 | 1 | R | VArRtg_SF | VArRtg_SF | sunssf |  |  | Scale factor |  | M
13 | 13 | 1 | R | ARtg | ARtg | uint16 | A | ARtg_SF | Maximum RMS AC current level capability of the inverter. | Sum of all connected phases. Current rating under nominal voltage under nominal power factor. | M
14 | 14 | 1 | R | ARtg_SF | ARtg_SF | sunssf |  |  | Scale factor |  | M
15 | 15 | 1 | R | PFRtgQ1 | PFRtgQ1 | int16 | cos() | PFRtg_SF | Minimum power factor capability of the inverter in quadrant 1. |  | M
16 | 16 | 1 | R | PFRtgQ2 | PFRtgQ2 | int16 | cos() | PFRtg_SF | Minimum power factor capability of the inverter in quadrant 2. |  | M
17 | 17 | 1 | R | PFRtgQ3 | PFRtgQ3 | int16 | cos() | PFRtg_SF | Minimum power factor capability of the inverter in quadrant 3. |  | M
18 | 18 | 1 | R | PFRtgQ4 | PFRtgQ4 | int16 | cos() | PFRtg_SF | Minimum power factor capability of the inverter in quadrant 4. |  | M
19 | 19 | 1 | R | PFRtg_SF | PFRtg_SF | sunssf |  |  | Scale factor |  | M
20 | 20 | 1 | R | PFSignR | PFSignR | enum16 |  |  | Sign convention for Power Factor settings: IEC=1 EEI=2. |  | M
21 | 21 | 1 | R | WHRtg | WHRtg | uint16 | Wh | WHRtg_SF | Nominal energy rating of storage device. |  | O
22 | 22 | 1 | R | WHRtg_SF | WHRtg_SF | sunssf |  |  | Scale factor |  | O
23 | 23 | 1 | R | AhrRtg | AhrRtg | uint16 | AH | AhrRtg_SF | The useable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). |  | O
24 | 24 | 1 | R | AhrRtg_SF | AhrRtg_SF | sunssf |  |  | Scale factor for amp-hour rating. |  | O
25 | 25 | 1 | R | MaxChaRte | MaxChaRte | uint16 | W | MaxChaRte_SF | Maximum rate of energy transfer into the storage device. |  | O
26 | 26 | 1 | R | MaxChaRte_SF | MaxChaRte_SF | sunssf |  |  | Scale factor |  | O
27 | 27 | 1 | R | MaxDisChaRte | MaxDisChaRte | uint16 | W | MaxDisChaRte_SF | Maximum rate of energy transfer out of the storage device. |  | O
28 | 28 | 1 | R | MaxDisChaRte_SF | MaxDisChaRte_SF | sunssf |  |  | Scale factor |  | O
// DERTyp enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
PV |  |  | 4
PV_STOR |  |  | 82
// PFSignR enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
IEC |  |  | 1
EEI |  |  | 2

## IC 121
// 121-Basic Settings : Inverter Controls Basic Settings (Ref 3: 8.4.2.1, Ref 4: 17)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 32 |  | M
// 121 Basic Settings Fixed Block (32)
3 | 3 | 1 | RW | WMax | WMax | uint16 | W | VAMax_SF | Setting for maximum power output. Default to WRtg. |  | M
4 | 4 | 1 | RW | VRef | VRef | uint16 | V | VRef_SF | Voltage at the PCC. |  | M
5 | 5 | 1 | RW | VRefOfs | VRefOfs | int16 | V | VRefOfs_SF | Offset from PCC to inverter. |  | M
6 | 6 | 1 | RW | VMax | VMax | uint16 | V | VMinMax_SF | Setpoint for maximum voltage. |  | O
7 | 7 | 1 | RW | VMin | VMin | uint16 | V | VMinMax_SF | Setpoint for minimum voltage. |  | O
8 | 8 | 1 | RW | VAMax | VAMax | uint16 | VA | VAMax_SF | Setpoint for maximum apparent power. Default to VARtg. |  | O
9 | 9 | 1 | RW | VArMaxQ1 | VArMaxQ1 | int16 | var | VArMax_SF | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. |  | O
10 | 10 | 1 | RW | VArMaxQ2 | VArMaxQ2 | int16 | var | VArMax_SF | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. |  | O
11 | 11 | 1 | RW | VArMaxQ3 | VArMaxQ3 | int16 | var | VArMax_SF | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. |  | O
12 | 12 | 1 | RW | VArMaxQ4 | VArMaxQ4 | int16 | var | VArMax_SF | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. |  | O
13 | 13 | 1 | RW | WGra | WGra | uint16 | % WMax/min | WGra_SF | Default ramp rate of change of active power due to command or internal action. |  | O
14 | 14 | 1 | RW | PFSign | PFSign | enum16 |  |  | Sign convention for Power Factor settings: IEC=1 EEI=2. |  | O
15 | 15 | 1 | RW | PFMinQ1 | PFMinQ1 | int16 | cos() | PFMin_SF | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. |  | O
16 | 16 | 1 | RW | PFMinQ2 | PFMinQ2 | int16 | cos() | PFMin_SF | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. |  | O
17 | 17 | 1 | RW | PFMinQ3 | PFMinQ3 | int16 | cos() | PFMin_SF | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. |  | O
18 | 18 | 1 | RW | PFMinQ4 | PFMinQ4 | int16 | cos() | PFMin_SF | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. |  | O
19 | 19 | 1 | RW | VArAct | VArAct | enum16 |  |  | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. |  | O
20 | 20 | 1 | RW | ClcTotVA | ClcTotVA | enum16 |  |  | Calculation method for total apparent power. 1=vector 2=arithmetic. |  | O
21 | 21 | 1 | RW | MaxRmpRte | MaxRmpRte | uint16 | % WGra | MaxRmpRte_SF | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. |  | O
22 | 22 | 1 | RW | ECPNomHz | ECPNomHz | uint16 | Hz | ECPNomHz_SF | Setpoint for nominal frequency at the ECP. |  | O
23 | 23 | 1 | RW | ConnPh | ConnPh | enum16 |  |  | Identity of connected phase for single phase inverters. A=1 B=2 C=3. |  | O
24 | 24 | 1 | R | WMax_SF | WMax_SF | sunssf |  |  | Scale factor for real power. |  | M
25 | 25 | 1 | R | VRef_SF | VRef_SF | sunssf |  |  | Scale factor for voltage at the PCC. |  | M
26 | 26 | 1 | R | VRefOfs_SF | VRefOfs_SF | sunssf |  |  | Scale factor for offset voltage. |  | M
27 | 27 | 1 | R | VMinMax_SF | VMinMax_SF | sunssf |  |  | Scale factor for min/max voltages. |  | O
28 | 28 | 1 | R | VAMax_SF | VAMax_SF | sunssf |  |  | Scale factor for apparent power. |  | O
29 | 29 | 1 | R | VArMax_SF | VArMax_SF | sunssf |  |  | Scale factor for reactive power. |  | O
30 | 30 | 1 | R | WGra_SF | WGra_SF | sunssf |  |  | Scale factor for default ramp rate. |  | O
31 | 31 | 1 | R | PFMin_SF | PFMin_SF | sunssf |  |  | Scale factor for minimum power factor. |  | O
32 | 32 | 1 | R | MaxRmpRte_SF | MaxRmpRte_SF | sunssf |  |  | Scale factor for maximum ramp percentage. |  | O
33 | 33 | 1 | R | ECPNomHz_SF | ECPNomHz_SF | sunssf |  |  | Scale factor for nominal frequency. |  | O
34 | 34 | 1 | R | Pad | Pad | pad |  |  | Pad register. |  | O
// PFSign enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
IEC |  |  | 1
EEI |  |  | 2
// VArAct enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
SWITCH |  |  | 1
MAINTAIN |  |  | 2
// ClcTotVA enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
VECTOR |  |  | 1
ARITHMETIC |  |  | 2
// ConnPh enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
A |  |  | 1
B |  |  | 2
C |  |  | 3

## IC 122
// 122-Measurements_Status : Inverter Controls Extended Measurements and Status (Ref 3: 8.14.3.2, Ref 4: 17)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 42 |  | M
// 122 Measurements_Status Fixed Block (42)
3 | 3 | 1 | R | PVConn | PVConn | bitfield16 |  |  | PV inverter present/available status. Enumerated value. |  | M
4 | 4 | 1 | R | StorConn | StorConn | bitfield16 |  |  | Storage inverter present/available status. Enumerated value. |  | M
5 | 5 | 1 | R | ECPConn | ECPConn | bitfield16 |  |  | ECP connection status: disconnected=0 connected=1. |  | M
6 | 9 | 4 | R | ActWh | ActWh | acc64 | Wh |  | AC lifetime active (real) energy output. |  | O
10 | 13 | 4 | R | ActVAh | ActVAh | acc64 | VAh |  | AC lifetime apparent energy output. |  | O
14 | 17 | 4 | R | ActVArhQ1 | ActVArhQ1 | acc64 | varh |  | AC lifetime reactive energy output in quadrant 1. |  | O
18 | 21 | 4 | R | ActVArhQ2 | ActVArhQ2 | acc64 | varh |  | AC lifetime reactive energy output in quadrant 2. |  | O
22 | 25 | 4 | R | ActVArhQ3 | ActVArhQ3 | acc64 | varh |  | AC lifetime negative energy output in quadrant 3. |  | O
26 | 29 | 4 | R | ActVArhQ4 | ActVArhQ4 | acc64 | varh |  | AC lifetime reactive energy output in quadrant 4. |  | O
30 | 30 | 1 | R | VArAval | VArAval | uint16 | var | VArAval_SF | Amount of VARs available without impacting watts output. |  | O
31 | 31 | 1 | R | VArAval_SF | VArAval_SF | sunssf |  |  | Scale factor for available VARs. |  | O
32 | 32 | 1 | R | WAval | WAval | uint16 | var | WAval_SF | Amount of Watts available. |  | O
33 | 33 | 1 | R | WAval_SF | WAval_SF | sunssf |  |  | Scale factor for available Watts. |  | O
34 | 35 | 2 | RW | StSetLimMsk | StSetLimMsk | bitfield32 |  |  | Bit Mask indicating setpoint limit(s) reached. Bits are persistent and must be cleared by the controller. |  | O
36 | 37 | 2 | R | StActCtl | StActCtl | bitfield32 |  |  | Bit Mask indicating which inverter controls are currently active. |  | O
38 | 41 | 4 | R | TmSrc | TmSrc | string |  |  | Source of time synchronization. |  | O
42 | 43 | 2 | R | Tms | Tms | uint32 | Secs |  | Seconds since 01-01-2000 00:00 UTC |  | O
44 | 44 | 1 | R | VrtSt |  | bitfield16 |  |  |  |  | O
// PVConn bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
CONNECTED |  |  | 0
AVAILABLE |  |  | 1
OPERATING |  |  | 2
TEST |  |  | 3
// StorConn bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
CONNECTED |  |  | 0
AVAILABLE |  |  | 1
OPERATING |  |  | 2
TEST |  |  | 3
// ECPConn bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
CONNECTED |  |  | 0
// StSetLimMsk bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
WMax |  |  | 0
VAMax |  |  | 1
VArPosMax |  |  | 2
VArNegMax |  |  | 3
VArAval |  |  | 4
PFLeadMin |  |  | 5
PFLagMin |  |  | 6
// StActCtl bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
FixedW |  |  | 0
FixedVAR |  |  | 1
FixedPF |  |  | 2
Volt-VAr |  |  | 3
Freq-Watt-Param |  |  | 4
Freq-Watt-Curve |  |  | 5
Dyn-Reactive-Current |  |  | 6
LVRT |  |  | 7
HVRT |  |  | 8
Watt-PF |  |  | 9
Volt-Watt |  |  | 10
Scheduled |  |  | 12
// VrtSt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
LVRT_ACTIVE |  |  | 0
HVRT_ACTIVE |  |  | 1

## IC 123
// 123-Immediate Controls : Immediate Inverter Controls (Ref 3: 8.7.1.2, 8.7.2.2, 8.7.3.2)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 26 |  | M
// 123 Immediate Controls Fixed Block (26)
3 | 3 | 1 | RW | Conn_WinTms | Conn_WinTms | uint16 | Secs |  | Time window for connect/disconnect. |  | O
4 | 4 | 1 | RW | Conn_RvrtTms | Conn_RvrtTms | uint16 | Secs |  | Timeout period for connect/disconnect. |  | O
5 | 5 | 1 | RW | Conn | Conn | enum16 |  |  | Enumerated valued. Connection control. |  | M
6 | 6 | 1 | RW | WMaxLimPct | WMaxLimPct | uint16 | % WMax | WMaxLimPct_SF | Set power output to specified level. |  | M
7 | 7 | 1 | RW | WMaxLimPct_WinTms | WMaxLimPct_WinTms | uint16 | Secs |  | Time window for power limit change. |  | O
8 | 8 | 1 | RW | WMaxLimPct_RvrtTms | WMaxLimPct_RvrtTms | uint16 | Secs |  | Timeout period for power limit. |  | O
9 | 9 | 1 | RW | WMaxLimPct_RmpTms | WMaxLimPct_RmpTms | uint16 | Secs |  | Ramp time for moving from current setpoint to new setpoint. |  | O
10 | 10 | 1 | RW | WMaxLim_Ena | WMaxLim_Ena | enum16 |  |  | Enumerated valued. Throttle enable/disable control. |  | M
11 | 11 | 1 | RW | OutPFSet | OutPFSet | int16 | cos() | OutPFSet_SF | Set power factor to specific value - cosine of angle. |  | M
12 | 12 | 1 | RW | PFExt | PFExt | enum16 |  |  | Enumerated value. Power Factor excitation |  | O
13 | 13 | 1 | RW | OutPFSet_WinTms | OutPFSet_WinTms | uint16 | Secs |  | Time window for power factor change. |  | O
14 | 14 | 1 | RW | OutPFSet_RvrtTms | OutPFSet_RvrtTms | uint16 | Secs |  | Timeout period for power factor. |  | O
15 | 15 | 1 | RW | OutPFSet_RmpTms | OutPFSet_RmpTms | uint16 | Secs |  | Ramp time for moving from current setpoint to new setpoint. |  | O
16 | 16 | 1 | RW | OutPFSet_Ena | OutPFSet_Ena | enum16 |  |  | Enumerated valued. Fixed power factor enable/disable control. |  | M
17 | 17 | 1 | RW | VArWMaxPct | VArWMaxPct | int16 | % WMax | VArPct_SF | Reactive power in percent of WMax. |  | O
18 | 18 | 1 | RW | VArMaxPct | VArMaxPct | int16 | % VArMax | VArPct_SF | Reactive power in percent of VArMax. |  | O
19 | 19 | 1 | RW | VArAvalPct | VArAvalPct | int16 | % VArAval | VArPct_SF | Reactive power in percent of VArAval. |  | O
20 | 20 | 1 | RW | VArPct_WinTms | VArPct_WinTms | uint16 | Secs |  | Time window for VAR limit change. |  | O
21 | 21 | 1 | RW | VArPct_RvrtTms | VArPct_RvrtTms | uint16 | Secs |  | Timeout period for VAR limit. |  | O
22 | 22 | 1 | RW | VArPct_RmpTms | VArPct_RmpTms | uint16 | Secs |  | Ramp time for moving from current setpoint to new setpoint. |  | O
23 | 23 | 1 | RW | VArPct_Mod |  | enum16 |  |  |  |  | O
24 | 24 | 1 | RW | VArPct_Ena |  | enum16 |  |  |  |  | M
25 | 25 | 1 | R | WMaxLimPct_SF | WMaxLimPct_SF | sunssf |  |  | Scale factor for power output percent. |  | M
26 | 26 | 1 | R | OutPFSet_SF | OutPFSet_SF | sunssf |  |  | Scale factor for power factor. |  | M
27 | 27 | 1 | R | VArPct_SF | VArPct_SF | sunssf |  |  | Scale factor for reactive power percent. |  | O
28 | 28 | 1 | R | Pad |  | pad |  |  |  |  | O
// Conn enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
DISCONNECT |  |  | 0
CONNECT |  |  | 1
// WMaxLim_Ena enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
DISABLED |  |  | 0
ENABLED |  |  | 1
// PFExt enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
OVER |  |  | 0
UNDER |  |  | 1
// OutPFSet_Ena enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
DISABLED |  |  | 0
ENABLED |  |  | 1
// VArPct_Mod enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
NONE |  |  | 0
WMax |  |  | 1
VArMax |  |  | 2
VArAval |  |  | 3
// VArPct_Ena enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
DISABLED |  |  | 0
ENABLED |  |  | 1

## IC 124
// 124-Storage : Basic Storage Controls (Ref 3: 8.7.4.2)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 24 |  | M
// 124 Storage Fixed Block (24)
3 | 3 | 1 | RW | WChaMax | WChaMax | uint16 | W | WChaMax_SF | Setpoint for maximum charge. |  | M
4 | 4 | 1 | RW | WChaGra | WChaGra | uint16 | % WChaMax/sec | WChaDisChaGra_SF | Setpoint for maximum charging rate. Default is MaxChaRte. |  | M
5 | 5 | 1 | RW | WDisChaGra | WDisChaGra | uint16 | % WChaMax/sec | WChaDisChaGra_SF | Setpoint for maximum discharge rate. Default is MaxDisChaRte. |  | M
6 | 6 | 1 | RW | StorCtl_Mod | StorCtl_Mod | bitfield16 |  |  | Activate hold/discharge/charge storage control mode. Bitfield value. |  | M
7 | 7 | 1 | RW | VAChaMax | VAChaMax | uint16 | VA | VAChaMax_SF | Setpoint for maximum charging VA. |  | O
8 | 8 | 1 | RW | MinRsvPct | MinRsvPct | uint16 | % WChaMax | MinRsvPct_SF | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage. |  | O
9 | 9 | 1 | R | ChaState | ChaState | uint16 | % AhrRtg | ChaState_SF | Currently available energy as a percent of the capacity rating. |  | O
10 | 10 | 1 | R | StorAval | StorAval | uint16 | AH | StorAval_SF | State of charge (ChaState) minus storage reserve (MinRsvPct) times capacity rating (AhrRtg). |  | O
11 | 11 | 1 | R | InBatV | InBatV | uint16 | V | InBatV_SF | Internal battery voltage. |  | O
12 | 12 | 1 | R | ChaSt | ChaSt | enum16 |  |  | Charge status of storage device. Enumerated value. |  | O
13 | 13 | 1 | RW | OutWRte | OutWRte | int16 | % WDisChaMax | InOutWRte_SF | Percent of max discharge rate. |  | O
14 | 14 | 1 | RW | InWRte | InWRte | int16 | % WChaMax | InOutWRte_SF | Percent of max charging rate. |  | O
15 | 15 | 1 | RW | InOutWRte_WinTms | InOutWRte_WinTms | uint16 | Secs |  | Time window for charge/discharge rate change. |  | O
16 | 16 | 1 | RW | InOutWRte_RvrtTms | InOutWRte_RvrtTms | uint16 | Secs |  | Timeout period for charge/discharge rate. |  | O
17 | 17 | 1 | RW | InOutWRte_RmpTms | InOutWRte_RmpTms | uint16 | Secs |  | Ramp time for moving from current setpoint to new setpoint. |  | O
18 | 18 | 1 | RW | ChaGriSet |  | enum16 |  |  |  |  | O
19 | 19 | 1 | R | WChaMax_SF | WChaMax_SF | sunssf |  |  | Scale factor for maximum charge. |  | M
20 | 20 | 1 | R | WChaDisChaGra_SF | WChaDisChaGra_SF | sunssf |  |  | Scale factor for maximum charge and discharge rate. |  | M
21 | 21 | 1 | R | VAChaMax_SF | VAChaMax_SF | sunssf |  |  | Scale factor for maximum charging VA. |  | O
22 | 22 | 1 | R | MinRsvPct_SF | MinRsvPct_SF | sunssf |  |  | Scale factor for minimum reserve percentage. |  | O
23 | 23 | 1 | R | ChaState_SF | ChaState_SF | sunssf |  |  | Scale factor for available energy percent. |  | O
24 | 24 | 1 | R | StorAval_SF | StorAval_SF | sunssf |  |  | Scale factor for state of charge. |  | O
25 | 25 | 1 | R | InBatV_SF | InBatV_SF | sunssf |  |  | Scale factor for battery voltage. |  | O
26 | 26 | 1 | R | InOutWRte_SF | InOutWRte_SF | sunssf |  |  | Scale factor for percent charge/discharge rate. |  | O
// ChaSt enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
OFF |  |  | 1
EMPTY |  |  | 2
DISCHARGING |  |  | 3
CHARGING |  |  | 4
FULL |  |  | 5
HOLDING |  |  | 6
TESTING |  |  | 7
// ChaGriSet enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
PV |  |  | 0
GRID |  |  | 1
// StorCtl_Mod bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
CHARGE |  |  | 0
DiSCHARGE |  |  | 1

## IC 125
// 125-Pricing : Pricing Signal (Ref 3: 8.7.5.1; Ref 4: 6)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 125. Uniquely identifies this as a SunSpec Pricing Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 8 |  | M
// 125 Pricing Fixed Block (8)
3 | 3 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | Is price-based charge/dischage mode active? |  | M
4 | 4 | 1 | RW | SigType | SigType | enum16 |  |  | Meaning of the pricing signal. When a Price schedule is used, type must match the schedule range variable description. |  | O
5 | 5 | 1 | RW | Sig | Sig | int16 |  | Sig_SF | Utility/ESP specific pricing signal. Content depends on pricing signal type. When H/M/L type is specified. Low=0; Med=1; High=2. |  | M
6 | 6 | 1 | RW | WinTms | WinTms | uint16 | Secs |  | Time window for charge/discharge pricing change. |  | O
7 | 7 | 1 | RW | RvtTms | RvtTms | uint16 | Secs |  | Timeout period for charge/discharge pricing change. |  | O
8 | 8 | 1 | RW | RmpTms | RmpTms | uint16 | Secs |  | Ramp time for moving from current charge or discharge level to new level. |  | O
9 | 9 | 1 | R | Sig_SF | Sig_SF | sunssf |  |  | Pricing signal scale factor. |  | M
10 | 10 | 1 | R | Pad |  | pad |  |  |  |  | O
// SigType enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
UNKNOWN |  |  | 0 |  |  |  | Signal type is unknown or other type of value
ABSOLUTE |  |  | 1 |  |  |  | Signal is an absolute price value in local rate. E.g. 23 (cents/kWh)
RELATIVE |  |  | 2 |  |  |  | Signal is a relative price in local rate. E.g. -5 (cents/kWh)
MULTIPLIER |  |  | 3 |  |  |  | Signal is a price multiplier (percentage). E.g. 15 % uplift in the rate
LEVEL |  |  | 4 |  |  |  | Signal is a price level. E.g. 0=lowest 1=low 2=normal 3=high 4=highest
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLE |  |  | 0

## IC 126
// 126-Static Volt-VAR : Static Volt-VAR Arrays (Ref 3: 8.8.1.2)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 10+N*54 |  | M
// 126 Static Volt-VAR Fixed Block (10)
3 | 3 | 1 | RW | ActCrv | ActCrv | uint16 |  |  | Index of active curve. 0=no active curve. |  | M
4 | 4 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | Is Volt-VAR control active. |  | M
5 | 5 | 1 | RW | WinTms | WinTms | uint16 | Secs |  | Time window for volt-VAR change. |  | O
6 | 6 | 1 | RW | RvrtTms | RvrtTms | uint16 | Secs |  | Timeout period for volt-VAR curve selection. |  | O
7 | 7 | 1 | RW | RmpTms | RmpTms | uint16 | Secs |  | The time of the PT1 in seconds (time to accomplish a change of 95%). |  | O
8 | 8 | 1 | R | NCrv | NCrv | uint16 |  |  | Number of curves supported (recommend 4). |  | M
9 | 9 | 1 | R | NPt | NPt | uint16 |  |  | Number of curve points supported (maximum of 20). |  | M
10 | 10 | 1 | R | V_SF | V_SF | sunssf |  |  | Scale factor for percent VRef. |  | M
11 | 11 | 1 | R | DeptRef_SF | DeptRef_SF | sunssf |  |  | scale factor for dependent variable. |  | M
12 | 12 | 1 | R | RmpIncDec_SF | RmpIncDec_SF | sunssf |  |  | Scale factor for increment and decrement ramps. |  | O
// 126 Static Volt-VAR Repeating Block (54)
13 | 13 | 1 | RW | ActPt | ActPt | uint16 |  |  | Number of active points in array. |  | M
14 | 14 | 1 | RW | DeptRef | DeptRef | enum16 |  | DeptRef_SF | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval. |  | M
15 | 15 | 1 | RW | V1 | V1 | uint16 | % VRef | V_SF | Point 1 Volts. |  | M
16 | 16 | 1 | RW | VAr1 | VAr1 | int16 |  | DeptRef_SF | Point 1 VARs. |  | M
17 | 17 | 1 | RW | V2 | V2 | uint16 | % VRef | V_SF | Point 2 Volts. |  | O
18 | 18 | 1 | RW | VAr2 | VAr2 | int16 |  | DeptRef_SF | Point 2 VARs. |  | O
19 | 19 | 1 | RW | V3 | V3 | uint16 | % VRef | V_SF | Point 2 Volts. |  | O
20 | 20 | 1 | RW | VAr3 | VAr3 | int16 | Various | DeptRef_SF | Point 3 VARs. |  | O
21 | 21 | 1 | RW | V4 | V4 | uint16 |  | V_SF | Point 4 Volts. |  | O
22 | 22 | 1 | RW | VAr4 | VAr4 | int16 |  | DeptRef_SF | Point 4 VARs. |  | O
23 | 23 | 1 | RW | V5 | V5 | uint16 | % VRef | V_SF | Point 5 Volts. |  | O
24 | 24 | 1 | RW | VAr5 | VAr5 | int16 |  | DeptRef_SF | Point 5 VARs. |  | O
25 | 25 | 1 | RW | V6 | V6 | uint16 | % VRef | V_SF | Point 6 Volts. |  | O
26 | 26 | 1 | RW | VAr6 | VAr6 | int16 |  | DeptRef_SF | Point 6 VARs. |  | O
27 | 27 | 1 | RW | V7 | V7 | uint16 | % VRef | V_SF | Point 7 Volts. |  | O
28 | 28 | 1 | RW | VAr7 | VAr7 | int16 |  | DeptRef_SF | Point 7 VARs. |  | O
29 | 29 | 1 | RW | V8 | V8 | uint16 | % VRef | V_SF | Point 8 Volts. |  | O
30 | 30 | 1 | RW | VAr8 | VAr8 | int16 |  | DeptRef_SF | Point 8 VARs. |  | O
31 | 31 | 1 | RW | V9 | V9 | uint16 | % VRef | V_SF | Point 9 Volts. |  | O
32 | 32 | 1 | RW | VAr9 | VAr9 | int16 |  | DeptRef_SF | Point 9 VARs. |  | O
33 | 33 | 1 | RW | V10 | V10 | uint16 | % VRef | V_SF | Point 10 Volts. |  | O
34 | 34 | 1 | RW | VAr10 | VAr10 | int16 |  | DeptRef_SF | Point 10 VARs. |  | O
35 | 35 | 1 | RW | V11 | V11 | uint16 | % VRef | V_SF | Point 11 Volts. |  | O
36 | 36 | 1 | RW | VAr11 | VAr11 | int16 |  | DeptRef_SF | Point 11 VARs. |  | O
37 | 37 | 1 | RW | V12 | V12 | uint16 | % VRef | V_SF | Point 12 Volts. |  | O
38 | 38 | 1 | RW | VAr12 | VAr12 | int16 |  | DeptRef_SF | Point 12 VARs. |  | O
39 | 39 | 1 | RW | V13 | V13 | uint16 | % VRef | V_SF | Point 13 Volts. |  | O
40 | 40 | 1 | RW | VAr13 | VAr13 | int16 |  | DeptRef_SF | Point 13 VARs. |  | O
41 | 41 | 1 | RW | V14 | V14 | uint16 | % VRef | V_SF | Point 14 Volts. |  | O
42 | 42 | 1 | RW | VAr14 | VAr14 | int16 |  | DeptRef_SF | Point 14 VARs. |  | O
43 | 43 | 1 | RW | V15 | V15 | uint16 | % VRef | V_SF | Point 15 Volts. |  | O
44 | 44 | 1 | RW | VAr15 | VAr15 | int16 |  | DeptRef_SF | Point 15 VARs. |  | O
45 | 45 | 1 | RW | V16 | V16 | uint16 | % VRef | V_SF | Point 16 Volts. |  | O
46 | 46 | 1 | RW | VAr16 | VAr16 | int16 |  | DeptRef_SF | Point 16 VARs. |  | O
47 | 47 | 1 | RW | V17 | V17 | uint16 | % VRef | V_SF | Point 17 Volts. |  | O
48 | 48 | 1 | RW | VAr17 | VAr17 | int16 |  | DeptRef_SF | Point 17 VARs. |  | O
49 | 49 | 1 | RW | V18 | V18 | uint16 | % VRef | V_SF | Point 18 Volts. |  | O
50 | 50 | 1 | RW | VAr18 | VAr18 | int16 |  | DeptRef_SF | Point 18 VARs. |  | O
51 | 51 | 1 | RW | V19 | V19 | uint16 | % VRef | V_SF | Point 19 Volts. |  | O
52 | 52 | 1 | RW | VAr19 | VAr19 | int16 |  | DeptRef_SF | Point 19 VARs. |  | O
53 | 53 | 1 | RW | V20 | V20 | uint16 | % VRef | V_SF | Point 20 Volts. |  | O
54 | 54 | 1 | RW | VAr20 | VAr20 | int16 |  | DeptRef_SF | Point 20 VARs. |  | O
55 | 62 | 8 | RW | CrvNam | CrvNam | string |  |  | Optional description for curve. (Max 16 chars) |  | O
63 | 63 | 1 | RW | RmpTms | RmpTms | uint16 | Secs |  | The time of the PT1 in seconds (time to accomplish a change of 95%). |  | O
64 | 64 | 1 | RW | RmpDecTmm | RmpDecTmm | uint16 | % ref_value/min | RmpIncDec_SF | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef. |  | O
65 | 65 | 1 | RW | RmpIncTmm | RmpIncTmm | uint16 | % ref_value/min | RmpIncDec_SF | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef. |  | O
66 | 66 | 1 | R | ReadOnly | ReadOnly | enum16 |  |  | Boolean flag indicates if curve is read-only or can be modified. |  | M
// DeptRef enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
WMax |  |  | 1
VArMax |  |  | 2
VArAval |  |  | 3
// ReadOnly enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
READWRITE |  |  | 0
READONLY |  |  | 1
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0

## IC 127
// 127-Freq-Watt Param : Parameterized Frequency-Watt (Ref 3: 8.9.1.2, 8.9.4.2)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 10 |  | M
// 127 Freq-Watt Param Fixed Block (10)
3 | 3 | 1 | RW | WGra | WGra | uint16 | % PM/Hz | WGra_SF | The slope of the reduction in the maximum allowed watts output as a function of frequency. |  | M
4 | 4 | 1 | RW | HzStr | HzStr | int16 | Hz | HzStrStop_SF | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs. |  | M
5 | 5 | 1 | RW | HzStop | HzStop | int16 | Hz | HzStrStop_SF | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed. |  | M
6 | 6 | 1 | RW | HysEna | HysEna | bitfield16 |  |  | Enable hysterisis |  | M
7 | 7 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | Is Parameterized Frequency-Watt control active. |  | M
8 | 8 | 1 | RW | HzStopWGra | HzStopWGra | uint16 | % WMax/min | RmpIncDec_SF | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event. |  | O
9 | 9 | 1 | R | WGra_SF | WGra_SF | sunssf |  |  | Scale factor for output gradient. |  | O
10 | 10 | 1 | R | HzStrStop_SF | HzStrStop_SF | sunssf |  |  | Scale factor for frequency deviations. |  | O
11 | 11 | 1 | R | RmpIncDec_SF | RmpIncDec_SF | sunssf |  |  | Scale factor for increment and decrement ramps. |  | O
12 | 12 | 1 | R | Pad |  | pad |  |  |  |  | O
// HysEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0

## IC 128
// 128-Dynamic Reactive Current : Dynamic Reactive Current (Ref 3: 8.10.1.2; Ref 4: 12)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 14 |  | M
// 128 Dynamic Reactive Current Fixed Block (14)
3 | 3 | 1 | RW | ArGraMod | ArGraMod | enum16 |  |  | Indicates if gradients trend toward zero at the edges of the deadband or trend toward zero at the center of the deadband. |  | M
4 | 4 | 1 | RW | ArGraSag | ArGraSag | uint16 | %ARtg/%dV | ArGra_SF | The gradient used to increase capacitive dynamic current. A value of 0 indicates no additional reactive current support. |  | M
5 | 5 | 1 | RW | ArGraSwell | ArGraSwell | uint16 | %ARtg/%dV | ArGra_SF | The gradient used to increase inductive dynamic current. A value of 0 indicates no additional reactive current support. |  | M
6 | 6 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | Activate dynamic reactive current model |  | M
7 | 7 | 1 | RW | FilTms | FilTms | uint16 | Secs |  | The time window used to calculate the moving average voltage. |  | O
8 | 8 | 1 | RW | DbVMin | DbVMin | uint16 | % VRef | VRefPct_SF | The lower delta voltage limit for which negative voltage deviations less than this value no dynamic vars are produced. |  | O
9 | 9 | 1 | RW | DbVMax | DbVMax | uint16 | % VRef | VRefPct_SF | The upper delta voltage limit for which positive voltage deviations less than this value no dynamic current produced. |  | O
10 | 10 | 1 | RW | BlkZnV | BlkZnV | uint16 | % VRef | VRefPct_SF | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced. |  | O
11 | 11 | 1 | RW | HysBlkZnV | HysBlkZnV | uint16 | % VRef | VRefPct_SF | Hysteresis voltage used with BlkZnV. |  | O
12 | 12 | 1 | RW | BlkZnTmms | BlkZnTmms | uint16 | mSecs |  | Block zone time the time before which reactive current support remains active regardless of how low the voltage drops. |  | O
13 | 13 | 1 | RW | HoldTmms | HoldTmms | uint16 | mSecs |  | Hold time during which reactive current support continues after the average voltage has entered the dead zone. |  | O
14 | 14 | 1 | R | ArGra_SF | ArGra_SF | sunssf |  |  | Scale factor for the gradients. |  | M
15 | 15 | 1 | R | VRefPct_SF | VRefPct_SF | sunssf |  |  | Scale factor for the voltage zone and limit settings. |  | O
16 | 16 | 1 | R | Pad |  | pad |  |  |  |  | O
// ArGraMod enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
EDGE |  |  | 0
CENTER |  |  | 1
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0

## IC 129
// 129-LVRTD : LVRT Must Disconnect (Ref 4: 11)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 129. Uniquely identifies this as a SunSpec LVRTD Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 10+N*50 |  | M
// 129 LVRTD Fixed Block (10)
3 | 3 | 1 | RW | ActCrv | ActCrv | uint16 |  |  | Index of active curve. 0=no active curve. |  | M
4 | 4 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | LVRT control mode. Enable active curve. Bitfield value. |  | M
5 | 5 | 1 | RW | WinTms | WinTms | uint16 | Secs |  | Time window for LVRT change. | Setting is ignored for LVRT controls. | O
6 | 6 | 1 | RW | RvrtTms | RvrtTms | uint16 | Secs |  | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls. | O
7 | 7 | 1 | RW | RmpTms | RmpTms | uint16 | Secs |  | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls. | O
8 | 8 | 1 | R | NCrv | NCrv | uint16 |  |  | Number of curves supported (recommend 4). |  | M
9 | 9 | 1 | R | NPt | NPt | uint16 |  |  | Number of curve points supported (maximumn of 20). |  | M
10 | 10 | 1 | R | Tms_SF | Tms_SF | sunssf |  |  | Scale factor for duration. |  | M
11 | 11 | 1 | R | V_SF | V_SF | sunssf |  |  | Scale factor for percent VRef. |  | M
12 | 12 | 1 | R | Pad |  | pad |  |  |  |  | O
// 129 LVRTD Repeating Block (50)
13 | 13 | 1 | RW | ActPt | ActPt | uint16 |  |  | Number of active points in array. |  | M
14 | 14 | 1 | RW | Tms1 | Tms1 | uint16 | Secs | Tms_SF | Point 1 must disconnect duration. |  | M
15 | 15 | 1 | RW | V1 | V1 | uint16 | % VRef | V_SF | Point 1 must disconnect voltage. |  | M
16 | 16 | 1 | RW | Tms2 | Tms2 | uint16 | Secs | Tms_SF | Point 2 must disconnect duration. |  | O
17 | 17 | 1 | RW | V2 | V2 | uint16 | % VRef | V_SF | Point 2 must disconnect voltage. |  | O
18 | 18 | 1 | RW | Tms3 | Tms3 | uint16 | Secs | Tms_SF | Point 3 must disconnect duration. |  | O
19 | 19 | 1 | RW | V3 | V3 | uint16 | % VRef | V_SF | Point 3 must disconnect voltage. |  | O
20 | 20 | 1 | RW | Tms4 | Tms4 | uint16 | Secs | Tms_SF | Point 4 must disconnect duration. |  | O
21 | 21 | 1 | RW | V4 | V4 | uint16 | % VRef | V_SF | Point 4 must disconnect voltage. |  | O
22 | 22 | 1 | RW | Tms5 | Tms5 | uint16 | Secs | Tms_SF | Point 5 must disconnect duration. |  | O
23 | 23 | 1 | RW | V5 | V5 | uint16 | % VRef | V_SF | Point 5 must disconnect voltage. |  | O
24 | 24 | 1 | RW | Tms6 | Tms6 | uint16 | Secs | Tms_SF | Point 6 must disconnect duration. |  | O
25 | 25 | 1 | RW | V6 | V6 | uint16 | % VRef | V_SF | Point 6 must disconnect voltage. |  | O
26 | 26 | 1 | RW | Tms7 | Tms7 | uint16 | Secs | Tms_SF | Point 7 must disconnect duration. |  | O
27 | 27 | 1 | RW | V7 | V7 | uint16 | % VRef | V_SF | Point 7 must disconnect voltage. |  | O
28 | 28 | 1 | RW | Tms8 | Tms8 | uint16 | Secs | Tms_SF | Point 8 must disconnect duration. |  | O
29 | 29 | 1 | RW | V8 | V8 | uint16 | % VRef | V_SF | Point 8 must disconnect voltage. |  | O
30 | 30 | 1 | RW | Tms9 | Tms9 | uint16 | Secs | Tms_SF | Point 9 must disconnect duration. |  | O
31 | 31 | 1 | RW | V9 | V9 | uint16 | % VRef | V_SF | Point 9 must disconnect voltage. |  | O
32 | 32 | 1 | RW | Tms10 | Tms10 | uint16 | Secs | Tms_SF | Point 10 must disconnect duration. |  | O
33 | 33 | 1 | RW | V10 | V10 | uint16 | % VRef | V_SF | Point 10 must disconnect voltage. |  | O
34 | 34 | 1 | RW | Tms11 | Tms11 | uint16 | Secs | Tms_SF | Point 11 must disconnect duration. |  | O
35 | 35 | 1 | RW | V11 | V11 | uint16 | % VRef | V_SF | Point 11 must disconnect voltage. |  | O
36 | 36 | 1 | RW | Tms12 | Tms12 | uint16 | Secs | Tms_SF | Point 12 must disconnect duration. |  | O
37 | 37 | 1 | RW | V12 | V12 | uint16 | % VRef | V_SF | Point 12 must disconnect voltage. |  | O
38 | 38 | 1 | RW | Tms13 | Tms13 | uint16 | Secs | Tms_SF | Point 13 must disconnect duration. |  | O
39 | 39 | 1 | RW | V13 | V13 | uint16 | % VRef | V_SF | Point 13 must disconnect voltage. |  | O
40 | 40 | 1 | RW | Tms14 | Tms14 | uint16 | Secs | Tms_SF | Point 14 must disconnect duration. |  | O
41 | 41 | 1 | RW | V14 | V14 | uint16 | % VRef | V_SF | Point 14 must disconnect voltage. |  | O
42 | 42 | 1 | RW | Tms15 | Tms15 | uint16 | Secs | Tms_SF | Point 15 must disconnect duration. |  | O
43 | 43 | 1 | RW | V15 | V15 | uint16 | % VRef | V_SF | Point 15 must disconnect voltage. |  | O
44 | 44 | 1 | RW | Tms16 | Tms16 | uint16 | Secs | Tms_SF | Point 16 must disconnect duration. |  | O
45 | 45 | 1 | RW | V16 | V16 | uint16 | % VRef | V_SF | Point 16 must disconnect voltage. |  | O
46 | 46 | 1 | RW | Tms17 | Tms17 | uint16 | Secs | Tms_SF | Point 17 must disconnect duration. |  | O
47 | 47 | 1 | RW | V17 | V17 | uint16 | % VRef | V_SF | Point 17 must disconnect voltage. |  | O
48 | 48 | 1 | RW | Tms18 | Tms18 | uint16 | Secs | Tms_SF | Point 18 must disconnect duration. |  | O
49 | 49 | 1 | RW | V18 | V18 | uint16 | % VRef | V_SF | Point 18 must disconnect voltage. |  | O
50 | 50 | 1 | RW | Tms19 | Tms19 | uint16 | Secs | Tms_SF | Point 19 must disconnect duration. |  | O
51 | 51 | 1 | RW | V19 | V19 | uint16 | % VRef | V_SF | Point 19 must disconnect voltage. |  | O
52 | 52 | 1 | RW | Tms20 | Tms20 | uint16 | Secs | Tms_SF | Point 20 must disconnect duration. |  | O
53 | 53 | 1 | RW | V20 | V20 | uint16 | % VRef | V_SF | Point 20 must disconnect voltage. |  | O
54 | 61 | 8 | RW | CrvNam | CrvNam | string |  |  | Optional description for curve. |  | O
62 | 62 | 1 | R | ReadOnly | ReadOnly | enum16 |  |  | Enumerated value indicates if curve is read-only or can be modified. |  | M
// ReadOnly enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
READWRITE |  |  | 0
READONLY |  |  | 1
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0

## IC 130
// 130-HVRTD : HVRT Must Disconnect (Ref 4: 11)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 130. Uniquely identifies this as a SunSpec HVRTD Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 10+N*50 |  | M
// 130 HVRTD Fixed Block (10)
3 | 3 | 1 | RW | ActCrv | ActCrv | uint16 |  |  | Index of active curve. 0=no active curve. |  | M
4 | 4 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | HVRT control mode. Enable active curve. Bitfield value. |  | M
5 | 5 | 1 | RW | WinTms | WinTms | uint16 | Secs |  | Time window for HVRT change. | Setting is ignored for HVRT controls. | O
6 | 6 | 1 | RW | RvrtTms | RvrtTms | uint16 | Secs |  | Timeout period for HVRT curve selection. | Setting is ignored for HVRT controls. | O
7 | 7 | 1 | RW | RmpTms | RmpTms | uint16 | Secs |  | Ramp time for moving from current mode to new mode. | Setting is ignored for HVRT controls. | O
8 | 8 | 1 | R | NCrv | NCrv | uint16 |  |  | Number of curves supported (recommend 4). |  | M
9 | 9 | 1 | R | NPt | NPt | uint16 |  |  | Number of curve points supported (maximumn of 20). |  | M
10 | 10 | 1 | R | Tms_SF | Tms_SF | sunssf |  |  | Scale factor for duration. |  | M
11 | 11 | 1 | R | V_SF | V_SF | sunssf |  |  | Scale factor for percent VRef. |  | M
12 | 12 | 1 | R | Pad |  | pad |  |  |  |  | O
// 130 HVRTD Repeating Block (50)
13 | 13 | 1 | RW | ActPt | ActPt | uint16 |  |  | Number of active points in array. |  | M
14 | 14 | 1 | RW | Tms1 | Tms1 | uint16 | Secs | Tms_SF | Point 1 must disconnect duration. |  | M
15 | 15 | 1 | RW | V1 | V1 | uint16 | % VRef | V_SF | Point 1 must disconnect voltage. |  | M
16 | 16 | 1 | RW | Tms2 | Tms2 | uint16 | Secs | Tms_SF | Point 2 must disconnect duration. |  | O
17 | 17 | 1 | RW | V2 | V2 | uint16 | % VRef | V_SF | Point 2 must disconnect voltage. |  | O
18 | 18 | 1 | RW | Tms3 | Tms3 | uint16 | Secs | Tms_SF | Point 3 must disconnect duration. |  | O
19 | 19 | 1 | RW | V3 | V3 | uint16 | % VRef | V_SF | Point 3 must disconnect voltage. |  | O
20 | 20 | 1 | RW | Tms4 | Tms4 | uint16 | Secs | Tms_SF | Point 4 must disconnect duration. |  | O
21 | 21 | 1 | RW | V4 | V4 | uint16 | % VRef | V_SF | Point 4 must disconnect voltage. |  | O
22 | 22 | 1 | RW | Tms5 | Tms5 | uint16 | Secs | Tms_SF | Point 5 must disconnect duration. |  | O
23 | 23 | 1 | RW | V5 | V5 | uint16 | % VRef | V_SF | Point 5 must disconnect voltage. |  | O
24 | 24 | 1 | RW | Tms6 | Tms6 | uint16 | Secs | Tms_SF | Point 6 must disconnect duration. |  | O
25 | 25 | 1 | RW | V6 | V6 | uint16 | % VRef | V_SF | Point 6 must disconnect voltage. |  | O
26 | 26 | 1 | RW | Tms7 | Tms7 | uint16 | Secs | Tms_SF | Point 7 must disconnect duration. |  | O
27 | 27 | 1 | RW | V7 | V7 | uint16 | % VRef | V_SF | Point 7 must disconnect voltage. |  | O
28 | 28 | 1 | RW | Tms8 | Tms8 | uint16 | Secs | Tms_SF | Point 8 must disconnect duration. |  | O
29 | 29 | 1 | RW | V8 | V8 | uint16 | % VRef | V_SF | Point 8 must disconnect voltage. |  | O
30 | 30 | 1 | RW | Tms9 | Tms9 | uint16 | Secs | Tms_SF | Point 9 must disconnect duration. |  | O
31 | 31 | 1 | RW | V9 | V9 | uint16 | % VRef | V_SF | Point 9 must disconnect voltage. |  | O
32 | 32 | 1 | RW | Tms10 | Tms10 | uint16 | Secs | Tms_SF | Point 10 must disconnect duration. |  | O
33 | 33 | 1 | RW | V10 | V10 | uint16 | % VRef | V_SF | Point 10 must disconnect voltage. |  | O
34 | 34 | 1 | RW | Tms11 | Tms11 | uint16 | Secs | Tms_SF | Point 11 must disconnect duration. |  | O
35 | 35 | 1 | RW | V11 | V11 | uint16 | % VRef | V_SF | Point 11 must disconnect voltage. |  | O
36 | 36 | 1 | RW | Tms12 | Tms12 | uint16 | Secs | Tms_SF | Point 12 must disconnect duration. |  | O
37 | 37 | 1 | RW | V12 | V12 | uint16 | % VRef | V_SF | Point 12 must disconnect voltage. |  | O
38 | 38 | 1 | RW | Tms13 | Tms13 | uint16 | Secs | Tms_SF | Point 13 must disconnect duration. |  | O
39 | 39 | 1 | RW | V13 | V13 | uint16 | % VRef | V_SF | Point 13 must disconnect voltage. |  | O
40 | 40 | 1 | RW | Tms14 | Tms14 | uint16 | Secs | Tms_SF | Point 14 must disconnect duration. |  | O
41 | 41 | 1 | RW | V14 | V14 | uint16 | % VRef | V_SF | Point 14 must disconnect voltage. |  | O
42 | 42 | 1 | RW | Tms15 | Tms15 | uint16 | Secs | Tms_SF | Point 15 must disconnect duration. |  | O
43 | 43 | 1 | RW | V15 | V15 | uint16 | % VRef | V_SF | Point 15 must disconnect voltage. |  | O
44 | 44 | 1 | RW | Tms16 | Tms16 | uint16 | Secs | Tms_SF | Point 16 must disconnect duration. |  | O
45 | 45 | 1 | RW | V16 | V16 | uint16 | % VRef | V_SF | Point 16 must disconnect voltage. |  | O
46 | 46 | 1 | RW | Tms17 | Tms17 | uint16 | Secs | Tms_SF | Point 17 must disconnect duration. |  | O
47 | 47 | 1 | RW | V17 | V17 | uint16 | % VRef | V_SF | Point 17 must disconnect voltage. |  | O
48 | 48 | 1 | RW | Tms18 | Tms18 | uint16 | Secs | Tms_SF | Point 18 must disconnect duration. |  | O
49 | 49 | 1 | RW | V18 | V18 | uint16 | % VRef | V_SF | Point 18 must disconnect voltage. |  | O
50 | 50 | 1 | RW | Tms19 | Tms19 | uint16 | Secs | Tms_SF | Point 19 must disconnect duration. |  | O
51 | 51 | 1 | RW | V19 | V19 | uint16 | % VRef | V_SF | Point 19 must disconnect voltage. |  | O
52 | 52 | 1 | RW | Tms20 | Tms20 | uint16 | Secs | Tms_SF | Point 20 must disconnect duration. |  | O
53 | 53 | 1 | RW | V20 | V20 | uint16 | % VRef | V_SF | Point 20 must disconnect voltage. |  | O
54 | 61 | 8 | RW | CrvNam | CrvNam | string |  |  | Optional description for curve. |  | O
62 | 62 | 1 | R | ReadOnly | ReadOnly | enum16 |  |  | Enumerated value indicates if curve is read-only or can be modified. |  | M
// ReadOnly enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
READWRITE |  |  | 0
READONLY |  |  | 1
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0

## IC 131
// 131-Watt-PF : Watt-Power Factor (Ref 3: 8.11.1.2)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 10+N*74 |  | M
// 131 Watt-PF Fixed Block (10)
3 | 3 | 1 | RW | ActCrv | ActCrv | uint16 |  |  | Index of active curve. 0=no active curve. |  | O
4 | 4 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | Is watt-PF mode active. |  | M
5 | 5 | 1 | RW | WinTms | WinTms | uint16 | Secs |  | Time window for watt-PF change. |  | O
6 | 6 | 1 | RW | RvrtTms | RvrtTms | uint16 | Secs |  | Timeout period for watt-PF curve selection. |  | O
7 | 7 | 1 | RW | RmpTms | RmpTms | uint16 | Secs |  | Ramp time for moving from current mode to new mode. |  | O
8 | 8 | 1 | R | NCrv | NCrv | uint16 |  |  | Number of curves supported (recommend 4). |  | O
9 | 9 | 1 | R | NPt | NPt | uint16 |  |  | Max number of points in array. |  | M
10 | 10 | 1 | R | W_SF | W_SF | sunssf |  |  | Scale factor for percent WMax. |  | M
11 | 11 | 1 | R | PF_SF | PF_SF | sunssf |  |  | Scale factor for PF. |  | M
12 | 12 | 1 | R | RmpIncDec_SF | RmpIncDec_SF | sunssf |  |  | Scale factor for increment and decrement ramps. |  | O
// 131 Watt-PF Repeating Block (74)
13 | 13 | 1 | RW | ActPt | ActPt | uint16 |  |  | Number of active points in array. |  | M
14 | 14 | 1 | RW | W1 | W1 | uint16 | % WMax | W_SF | Point 1 Watts. |  | M
15 | 15 | 1 | RW | PF1 | PF1 | int16 | cos() | PF_SF | Point 1 PF. |  | M
16 | 16 | 1 | RW | PFExt1 | PFExt1 | enum16 |  |  | Powerfactor excitation |  | O
17 | 17 | 1 | RW | W2 | W2 | uint16 | % WMax | W_SF | Point 2 Watts. |  | O
18 | 18 | 1 | RW | PF2 | PF2 | int16 | cos() | PF_SF | Point 2 PF. |  | O
19 | 19 | 1 | RW | PFExt2 | PFExt2 | enum16 |  |  | Powerfactor excitation |  | O
20 | 20 | 1 | RW | W3 | W3 | uint16 | % WMax | W_SF | Point 3 Watts. |  | O
21 | 21 | 1 | RW | PF3 | PF3 | int16 | cos() | PF_SF | Point 3 PF. |  | O
22 | 22 | 1 | RW | PFExt3 | PFExt3 | enum16 |  |  | Powerfactor excitation |  | O
23 | 23 | 1 | RW | W4 | W4 | uint16 | % WMax | W_SF | Point 4 Watts. |  | O
24 | 24 | 1 | RW | PF4 | PF4 | int16 | cos() | PF_SF | Point 4 PF. |  | O
25 | 25 | 1 | RW | PFExt4 | PFExt4 | enum16 |  |  | Powerfactor excitation |  | O
26 | 26 | 1 | RW | W5 | W5 | uint16 | % WMax | W_SF | Point 5 Watts. |  | O
27 | 27 | 1 | RW | PF5 | PF5 | int16 | cos() | PF_SF | Point 5 PF. |  | O
28 | 28 | 1 | RW | PFExt5 | PFExt5 | enum16 |  |  | Powerfactor excitation |  | O
29 | 29 | 1 | RW | W6 | W6 | uint16 | % WMax | W_SF | Point 6 Watts. |  | O
30 | 30 | 1 | RW | PF6 | PF6 | int16 | cos() | PF_SF | Point 6 PF. |  | O
31 | 31 | 1 | RW | PFExt6 | PFExt6 | enum16 |  |  | Powerfactor excitation |  | O
32 | 32 | 1 | RW | W7 | W7 | uint16 | % WMax | W_SF | Point 7 Watts. |  | O
33 | 33 | 1 | RW | PF7 | PF7 | int16 | cos() | PF_SF | Point 7 PF. |  | O
34 | 34 | 1 | RW | PFExt7 | PFExt7 | enum16 |  |  | Powerfactor excitation |  | O
35 | 35 | 1 | RW | W8 | W8 | uint16 | % WMax | W_SF | Point 8 Watts. |  | O
36 | 36 | 1 | RW | PF8 | PF8 | int16 | cos() | PF_SF | Point 8 PF. |  | O
37 | 37 | 1 | RW | PFExt8 | PFExt8 | enum16 |  |  | Powerfactor excitation |  | O
38 | 38 | 1 | RW | W9 | W9 | uint16 | % WMax | W_SF | Point 9 Watts. |  | O
39 | 39 | 1 | RW | PF9 | PF9 | int16 | cos() | PF_SF | Point 9 PF. |  | O
40 | 40 | 1 | RW | PFExt9 | PFExt9 | enum16 |  |  | Powerfactor excitation |  | O
41 | 41 | 1 | RW | W10 | W10 | uint16 | % WMax | W_SF | Point 10 Watts. |  | O
42 | 42 | 1 | RW | PF10 | PF10 | int16 | cos() | PF_SF | Point 10 PF. |  | O
43 | 43 | 1 | RW | PFExt10 | PFExt10 | enum16 |  |  | Powerfactor excitation |  | O
44 | 44 | 1 | RW | W11 |  | uint16 | % WMax | W_SF |  |  | O
45 | 45 | 1 | RW | PF11 |  | int16 | cos() | PF_SF |  |  | O
46 | 46 | 1 | RW | PFExt11 |  | enum16 |  |  |  |  | O
47 | 47 | 1 | RW | W12 |  | uint16 | % WMax | W_SF |  |  | O
48 | 48 | 1 | RW | PF12 |  | int16 | cos() | PF_SF |  |  | O
49 | 49 | 1 | RW | PFExt12 |  | enum16 |  |  |  |  | O
50 | 50 | 1 | RW | W13 |  | uint16 | % WMax | W_SF |  |  | O
51 | 51 | 1 | RW | PF13 |  | int16 | cos() | PF_SF |  |  | O
52 | 52 | 1 | RW | PFExt13 |  | enum16 |  |  |  |  | O
53 | 53 | 1 | RW | W14 |  | uint16 | % WMax | W_SF |  |  | O
54 | 54 | 1 | RW | PF14 |  | int16 | cos() | PF_SF |  |  | O
55 | 55 | 1 | RW | PFExt14 |  | enum16 |  |  |  |  | O
56 | 56 | 1 | RW | W15 |  | uint16 | % WMax | W_SF |  |  | O
57 | 57 | 1 | RW | PF15 |  | int16 | cos() | PF_SF |  |  | O
58 | 58 | 1 | RW | PFExt15 |  | enum16 |  |  |  |  | O
59 | 59 | 1 | RW | W16 |  | uint16 | % WMax | W_SF |  |  | O
60 | 60 | 1 | RW | PF16 |  | int16 | cos() | PF_SF |  |  | O
61 | 61 | 1 | RW | PFExt16 |  | enum16 |  |  |  |  | O
62 | 62 | 1 | RW | W17 |  | uint16 | % WMax | W_SF |  |  | O
63 | 63 | 1 | RW | PF17 |  | int16 | cos() | PF_SF |  |  | O
64 | 64 | 1 | RW | PFExt17 |  | enum16 |  |  |  |  | O
65 | 65 | 1 | RW | W18 |  | uint16 | % WMax | W_SF |  |  | O
66 | 66 | 1 | RW | PF18 |  | int16 | cos() | PF_SF |  |  | O
67 | 67 | 1 | RW | PFExt18 |  | enum16 |  |  |  |  | O
68 | 68 | 1 | RW | W19 |  | uint16 | % WMax | W_SF |  |  | O
69 | 69 | 1 | RW | PF19 |  | int16 | cos() | PF_SF |  |  | O
70 | 70 | 1 | RW | PFExt19 |  | enum16 |  |  |  |  | O
71 | 71 | 1 | RW | W20 |  | uint16 | % WMax | W_SF |  |  | O
72 | 72 | 1 | RW | PF20 |  | int16 | cos() | PF_SF |  |  | O
73 | 73 | 1 | RW | PFExt20 |  | enum16 |  |  |  |  | O
74 | 81 | 8 | RW | CrvNam | CrvNam | string |  |  | Optional description for curve. |  | O
82 | 82 | 1 | RW | RmpPT1Tms | RmpPT1Tms | uint16 | Secs |  | The time of the PT1 in seconds (time to accomplish a change of 95%). |  | O
83 | 83 | 1 | RW | RmpDecTmm | RmpDecTmm | uint16 | % PF/min | RmpIncDec_SF | The maximum rate at which the power factor may be reduced in response to changes in the power value. |  | O
84 | 84 | 1 | RW | RmpIncTmm | RmpIncTmm | uint16 | % PF/min | RmpIncDec_SF | The maximum rate at which the power factor may be increased in response to changes in the power value. |  | O
85 | 85 | 1 | R | ReadOnly | ReadOnly | enum16 |  |  | Enumerated value indicates if curve is read-only or can be modified. |  | M
86 | 86 | 1 | R | Pad |  | pad |  |  |  |  | O
// ReadOnly enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
READWRITE |  |  | 0
READONLY |  |  | 1
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0

## IC 132
// 132-Volt-Watt : Volt-Watt (Ref 3: 8.12.1.2)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 10+N*54 |  | M
// 132 Volt-Watt Fixed Block (10)
3 | 3 | 1 | RW | ActCrv | ActCrv | uint16 |  |  | Index of active curve. 0=no active curve. |  | M
4 | 4 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | Is Volt-Watt control active. |  | M
5 | 5 | 1 | RW | WinTms | WinTms | uint16 | Secs |  | Time window for volt-watt change. |  | O
6 | 6 | 1 | RW | RvrtTms | RvrtTms | uint16 | Secs |  | Timeout period for volt-watt curve selection. |  | O
7 | 7 | 1 | RW | RmpTms | RmpTms | uint16 | Secs |  | Ramp time for moving from current mode to new mode. |  | O
8 | 8 | 1 | R | NCrv | NCrv | uint16 |  |  | Number of curves supported (recommend min. 4). |  | M
9 | 9 | 1 | R | NPt | NPt | uint16 |  |  | Number of points in array (maximum 20). |  | M
10 | 10 | 1 | R | V_SF | V_SF | sunssf |  |  | Scale factor for percent VRef. |  | M
11 | 11 | 1 | R | DeptRef_SF | DeptRef_SF | sunssf |  |  | Scale Factor for % DeptRef |  | M
12 | 12 | 1 | R | RmpIncDec_SF | RmpIncDec_SF | sunssf |  |  | Scale factor for increment and decrement ramps. |  | O
// 132 Volt-Watt Repeating Block (54)
13 | 13 | 1 | RW | ActPt | ActPt | uint16 |  |  | Number of active points in array. |  | M
14 | 14 | 1 | RW | DeptRef | DeptRef | enum16 |  |  | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail |  | M
15 | 15 | 1 | RW | V1 | V1 | uint16 | % VRef | V_SF | Point 1 Volts. |  | M
16 | 16 | 1 | RW | W1 | W1 | int16 | % VRef | DeptRef_SF | Point 1 Watts. |  | M
17 | 17 | 1 | RW | V2 | V2 | uint16 | % VRef | V_SF | Point 2 Volts. |  | O
18 | 18 | 1 | RW | W2 | W2 | int16 | % VRef | DeptRef_SF | Point 2 Watts. |  | O
19 | 19 | 1 | RW | V3 | V3 | uint16 | % VRef | V_SF | Point 3 Volts. |  | O
20 | 20 | 1 | RW | W3 | W3 | int16 | % VRef | DeptRef_SF | Point 3 Watts. |  | O
21 | 21 | 1 | RW | V4 | V4 | uint16 | % VRef | V_SF | Point 4 Volts. |  | O
22 | 22 | 1 | RW | W4 | W4 | int16 | % VRef | DeptRef_SF | Point 4 Watts. |  | O
23 | 23 | 1 | RW | V5 | V5 | uint16 | % VRef | V_SF | Point 5 Volts. |  | O
24 | 24 | 1 | RW | W5 | W5 | int16 | % VRef | DeptRef_SF | Point 5 Watts. |  | O
25 | 25 | 1 | RW | V6 | V6 | uint16 | % VRef | V_SF | Point 6 Volts. |  | O
26 | 26 | 1 | RW | W6 | W6 | int16 | % VRef | DeptRef_SF | Point 6 Watts. |  | O
27 | 27 | 1 | RW | V7 | V7 | uint16 | % VRef | V_SF | Point 7 Volts. |  | O
28 | 28 | 1 | RW | W7 | W7 | int16 | % VRef | DeptRef_SF | Point 7 Watts. |  | O
29 | 29 | 1 | RW | V8 | V8 | uint16 | % VRef | V_SF | Point 8 Volts. |  | O
30 | 30 | 1 | RW | W8 | W8 | int16 | % VRef | DeptRef_SF | Point 8 Watts. |  | O
31 | 31 | 1 | RW | V9 | V9 | uint16 | % VRef | V_SF | Point 9 Volts. |  | O
32 | 32 | 1 | RW | W9 | W9 | int16 | % VRef | DeptRef_SF | Point 9 Watts. |  | O
33 | 33 | 1 | RW | V10 | V10 | uint16 | % VRef | V_SF | Point 10 Volts. |  | O
34 | 34 | 1 | RW | W10 | W10 | int16 | % VRef | DeptRef_SF | Point 10 Watts. |  | O
35 | 35 | 1 | RW | V11 | V11 | uint16 | % VRef | V_SF | Point 11 Volts. |  | O
36 | 36 | 1 | RW | W11 | W11 | int16 | % VRef | DeptRef_SF | Point 11 Watts. |  | O
37 | 37 | 1 | RW | V12 | V12 | uint16 | % VRef | V_SF | Point 12 Volts. |  | O
38 | 38 | 1 | RW | W12 | W12 | int16 | % VRef | DeptRef_SF | Point 12 Watts. |  | O
39 | 39 | 1 | RW | V13 | V13 | uint16 | % VRef | V_SF | Point 13 Volts. |  | O
40 | 40 | 1 | RW | W13 | W13 | int16 | % VRef | DeptRef_SF | Point 13 Watts. |  | O
41 | 41 | 1 | RW | V14 | V14 | uint16 | % VRef | V_SF | Point 14 Volts. |  | O
42 | 42 | 1 | RW | W14 | W14 | int16 | % VRef | DeptRef_SF | Point 14 Watts. |  | O
43 | 43 | 1 | RW | V15 | V15 | uint16 | % VRef | V_SF | Point 15 Volts. |  | O
44 | 44 | 1 | RW | W15 | W15 | int16 | % VRef | DeptRef_SF | Point 15 Watts. |  | O
45 | 45 | 1 | RW | V16 | V16 | uint16 | % VRef | V_SF | Point 16 Volts. |  | O
46 | 46 | 1 | RW | W16 | W16 | int16 | % VRef | DeptRef_SF | Point 16 Watts. |  | O
47 | 47 | 1 | RW | V17 | V17 | uint16 | % VRef | V_SF | Point 17 Volts. |  | O
48 | 48 | 1 | RW | W17 | W17 | int16 | % VRef | DeptRef_SF | Point 17 Watts. |  | O
49 | 49 | 1 | RW | V18 | V18 | uint16 | % VRef | V_SF | Point 18 Volts. |  | O
50 | 50 | 1 | RW | W18 | W18 | int16 | % VRef | DeptRef_SF | Point 18 Watts. |  | O
51 | 51 | 1 | RW | V19 | V19 | uint16 | % VRef | V_SF | Point 19 Volts. |  | O
52 | 52 | 1 | RW | W19 | W19 | int16 | % VRef | DeptRef_SF | Point 19 Watts. |  | O
53 | 53 | 1 | RW | V20 | V20 | uint16 | % VRef | V_SF | Point 20 Volts. |  | O
54 | 54 | 1 | RW | W20 | W20 | int16 | % VRef | DeptRef_SF | Point 20 Watts. |  | O
55 | 62 | 8 | RW | CrvNam | CrvNam | string |  |  | Optional description for curve. |  | O
63 | 63 | 1 | RW | RmpPt1Tms | RmpPt1Tms | uint16 | Secs |  | The time of the PT1 in seconds (time to accomplish a change of 95%). |  | O
64 | 64 | 1 | RW | RmpDecTmm | RmpDecTmm | uint16 | % WMax/min | RmpIncDec_SF | The maximum rate at which the watt value may be reduced in response to changes in the voltage value. |  | O
65 | 65 | 1 | RW | RmpIncTmm | RmpIncTmm | uint16 | % WMax/min | RmpIncDec_SF | The maximum rate at which the watt value may be increased in response to changes in the voltage value. |  | O
66 | 66 | 1 | R | ReadOnly | ReadOnly | enum16 |  |  | Enumerated value indicates if curve is read-only or can be modified. |  | M
// DeptRef enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
%WMax |  |  | 1
%WAval |  |  | 2
// ReadOnly enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
READWRITE |  |  | 0
READONLY |  |  | 1
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0

## IC 133
// 133-Basic Scheduling : Basic Scheduling (Ref 2: 2.2.8)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 133. Uniquely identifies this as a SunSpec Basic Scheduling Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 6+N*50 |  | M
// 133 Basic Scheduling Fixed Block (6)
3 | 4 | 2 | RW | ActSchd | ActSchd | bitfield32 |  |  | Bitfield of active schedules |  | M
5 | 5 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | Is basic scheduling active. |  | M
6 | 6 | 1 | R | NSchd | NSchd | uint16 |  |  | Number of schedules supported (recommend min. 4, max 32) |  | M
7 | 7 | 1 | R | NPts | NPts | uint16 |  |  | Number of schedule entries supuported (maximum of 10). |  | M
8 | 8 | 1 | R | Pad | Pad | pad |  |  | Pad register. |  | O
// 133 Basic Scheduling Repeating Block (50)
9 | 9 | 1 | RW | ActPts | ActPts | uint16 |  |  | Number of active entries in schedule. |  | M
10 | 11 | 2 | RW | StrTms | StrTms | uint32 | Secs |  | Schedule start in seconds since 2000 JAN 01 00:00:00 UTC. |  | M
12 | 12 | 1 | RW | SchdTyp | SchdTyp | enum16 |  |  | The repetition frequency for time-based schedules: no repeat=0 |  | M
13 | 13 | 1 | RW | XTyp | XTyp | enum16 |  |  | The meaning of the X-values in the array. |  | M
14 | 14 | 1 | RW | X_SF | X_SF | sunssf |  |  | Scale factor for schedule range values. |  | M
15 | 15 | 1 | RW | YTyp | YTyp | enum16 |  |  | The meaning of the Y-values in the array. |  | M
16 | 16 | 1 | RW | Y_SF | Y_SF | sunssf |  |  | Scale factor for schedule target values. |  | M
17 | 17 | 1 | RW | X1 | X1 | int16 |  | X_SF | Entry 1 range. |  | M
18 | 18 | 1 | RW | Y1.1 | Y1.1 | int16 |  | Y_SF | Entry 1 target. |  | M
19 | 19 | 1 | RW | Y1.2 | Y1.2 | int16 |  |  | Entry 1 target supplement. |  | O
20 | 20 | 1 | RW | X2 | X2 | int16 |  | X_SF | Entry 2 range. |  | O
21 | 21 | 1 | RW | Y2.1 | Y2.1 | int16 |  | Y_SF | Entry 2 target. |  | O
22 | 22 | 1 | RW | Y2.2 | Y2.2 | int16 |  |  | Entry 2 target supplement. |  | O
23 | 23 | 1 | RW | X3 | X3 | int16 |  | X_SF | Entry 3 range. |  | O
24 | 24 | 1 | RW | Y3.1 | Y3.1 | int16 |  | Y_SF | Entry 3 target. |  | O
25 | 25 | 1 | RW | Y3.2 | Y3.2 | int16 |  |  | Entry 3 target supplement. |  | O
26 | 26 | 1 | RW | X4 | X4 | int16 |  | X_SF | Entry 4 range. |  | O
27 | 27 | 1 | RW | Y4.1 | Y4.1 | int16 |  | Y_SF | Entry 4 target. |  | O
28 | 28 | 1 | RW | Y4.2 | Y4.2 | int16 |  |  | Entry 4 target supplement. |  | O
29 | 29 | 1 | RW | X5 | X5 | int16 |  | X_SF | Entry 15range. |  | O
30 | 30 | 1 | RW | Y5.1 | Y5.1 | int16 |  | Y_SF | Entry 5 target. |  | O
31 | 31 | 1 | RW | Y5.2 | Y5.2 | int16 |  |  | Entry 5 target supplement. |  | O
32 | 32 | 1 | RW | X6 | X6 | int16 |  | X_SF | Entry 6 range. |  | O
33 | 33 | 1 | RW | Y6.1 | Y6.1 | int16 |  | Y_SF | Entry 6 target. |  | O
34 | 34 | 1 | RW | Y6.2 | Y6.2 | int16 |  |  | Entry 6 target supplement. |  | O
35 | 35 | 1 | RW | X7 | X7 | int16 |  | X_SF | Entry 7 range. |  | O
36 | 36 | 1 | RW | Y7.1 | Y7.1 | int16 |  | Y_SF | Entry 7 target. |  | O
37 | 37 | 1 | RW | Y7.2 | Y7.2 | int16 |  |  | Entry 7 target supplement. |  | O
38 | 38 | 1 | RW | X8 | X8 | int16 |  | X_SF | Entry 8 range. |  | O
39 | 39 | 1 | RW | Y8.1 | Y8.1 | int16 |  | Y_SF | Entry 8 target. |  | O
40 | 40 | 1 | RW | Y8.2 | Y8.2 | int16 |  |  | Entry 8 target supplement. |  | O
41 | 41 | 1 | RW | X9 | X9 | int16 |  | X_SF | Entry 9 range. |  | O
42 | 42 | 1 | RW | Y9.1 | Y9.1 | int16 |  | Y_SF | Entry 9 target. |  | O
43 | 43 | 1 | RW | Y9.2 | Y9.2 | int16 |  |  | Entry 10 target supplement. |  | O
44 | 44 | 1 | RW | X10 | X10 | int16 |  | X_SF | Entry 10 range. |  | O
45 | 45 | 1 | RW | Y10.1 | Y10.1 | int16 |  | Y_SF | Entry 10 target. |  | O
46 | 46 | 1 | RW | Y10.2 | Y10.2 | int16 |  |  | Entry 10 target supplement. |  | O
47 | 54 | 8 | RW | Nam | Nam | string |  |  | Optional description for schedule. |  | O
55 | 55 | 1 | RW | WinTms | WinTms | uint16 | Secs |  | Time window for schedule entry change. |  | O
56 | 56 | 1 | RW | RmpTms | RmpTms | uint16 | Secs |  | Ramp time for moving from current target to new target. |  | O
57 | 57 | 1 | R | ActIndx | ActIndx | uint16 |  |  | Index of active entry in the active schedule. |  | M
58 | 58 | 1 | R | Pad | Pad | pad |  |  | Pad register. |  | O
// SchdTyp enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ONETIME |  |  | 0
DAILY |  |  | 1
WEEKLY |  |  | 2
MONTHLY |  |  | 3
WEEKDAY |  |  | 4
HOLIDAY |  |  | 5
// XTyp enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
UNSET |  |  | 0
TIME |  |  | 1
TEMP |  |  | 2
PRICE |  |  | 3
OTHER |  |  | 99
// YTyp enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
UNSET |  |  | 0
WMax |  |  | 1
RSRVD2 |  |  | 2
PF |  |  | 3
RSRVD4 |  |  | 4
WATT_PRICE |  |  | 5
VAR_PRICE |  |  | 6
RSRVD7 |  |  | 7
VOLT_VAR_ARRAY |  |  | 8
WChaGra |  |  | 9
WDisChaGra |  |  | 10
VArAval |  |  | 11
OTHER |  |  | 99
// ActSchd bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
SCHED1 |  |  | 0
SCHED2 |  |  | 1
SCHED3 |  |  | 2
SCHED4 |  |  | 3
SCHED5 |  |  | 4
SCHED6 |  |  | 5
SCHED7 |  |  | 6
SCHED8 |  |  | 7
SCHED9 |  |  | 8
SCHED10 |  |  | 9
SCHED12 |  |  | 10
SCHED13 |  |  | 11
SCHED14 |  |  | 12
SCHED15 |  |  | 13
SCHED16 |  |  | 14
SCHED17 |  |  | 15
SCHED18 |  |  | 16
SCHED19 |  |  | 17
SCHED20 |  |  | 18
SCHED21 |  |  | 19
SCHED22 |  |  | 21
SCHED23 |  |  | 22
SCHED24 |  |  | 23
SCHED25 |  |  | 24
SCHED26 |  |  | 25
SCHED27 |  |  | 26
SCHED28 |  |  | 27
SCHED29 |  |  | 28
SCHED30 |  |  | 29
SCHED31 |  |  | 30
SCHED32 |  |  | 31
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0

## IC 134
// 134-Freq-Watt Crv : Curve-Based Frequency-Watt (Ref 3: 8.9.1.2, 8.9.4.2)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 134. Uniquely identifies this as a SunSpec Freq-Watt Crv Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 16+N*54 |  | M
// 134 Freq-Watt Crv Fixed Block (16)
3 | 3 | 1 | RW | ActCrv | ActCrv | uint16 |  |  | Index of active curve. 0=no active curve. |  | M
4 | 4 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | Is curve-based Frequency-Watt control active. |  | M
5 | 5 | 1 | RW | SnptW | SnptW | bitfield16 |  |  | 1=enable snapshot/capture mode |  | M
6 | 6 | 1 | RW | WRef | WRef | uint16 | W | WMax_SF | Reference active power (default = WMax). |  | O
7 | 7 | 1 | RW | WRefStrHz | WRefStrHz | uint16 | Hz | HzStrStop_SF | Frequency deviation from nominal frequency at the time of the snapshot to start constraining power output. |  | O
8 | 8 | 1 | RW | WRefStopHz | WRefStopHz | uint16 | Hz | HzStrStop_SF | Frequency deviation from nominal frequency at which to release the power output. |  | O
9 | 9 | 1 | RW | RmpRsUp | RmpRsUp | uint16 | % WMax/min | RmpIncDec_SF | The maximum rate at which the power may be increased after releasing the frozen value of snap shot function. |  | O
10 | 10 | 1 | RW | WinTms | WinTms | uint16 | Secs |  | Time window for freq-watt change. |  | O
11 | 11 | 1 | RW | RvrtTms | RvrtTms | uint16 | Secs |  | Timeout period for freq-watt curve selection. |  | O
12 | 12 | 1 | RW | RmpTms | RmpTms | uint16 | Secs |  | Ramp time for moving from current mode to new mode. |  | O
13 | 13 | 1 | R | NCrv | NCrv | uint16 |  |  | Number of curves supported (recommend min. 4). |  | M
14 | 14 | 1 | R | NPt | NPt | uint16 |  |  | Number of curve points supported (maximum of 10). |  | M
15 | 15 | 1 | R | Hz_SF | Hz_SF | sunssf | SF |  | Scale factor for frequency. |  | M
16 | 16 | 1 | R | W_SF | W_SF | sunssf | SF |  | Scale factor for percent WRef. |  | M
17 | 17 | 1 | R | RmpIncDec_SF | RmpIncDec_SF | sunssf | SF |  | Scale factor for increment and decrement ramps. |  | O
18 | 18 | 1 | R | Pad | Pad | pad |  |  | Pad register. |  | O
// 134 Freq-Watt Crv Repeating Block (54)
19 | 19 | 1 | RW | ActPt | ActPt | uint16 |  |  | Number of active points in array. |  | M
20 | 20 | 1 | RW | Hz1 | Hz1 | uint16 | Hz | Hz_SF | Point 1 Hertz. |  | M
21 | 21 | 1 | RW | W1 | W1 | int16 | % WRef | W_SF | Point 1 Watts. |  | M
22 | 22 | 1 | RW | Hz2 | Hz2 | uint16 | Hz | Hz_SF | Point 2 Hertz. |  | O
23 | 23 | 1 | RW | W2 | W2 | int16 | % WRef | W_SF | Point 2 Watts. |  | O
24 | 24 | 1 | RW | Hz3 | Hz3 | uint16 | Hz | Hz_SF | Point 3 Hertz. |  | O
25 | 25 | 1 | RW | W3 | W3 | int16 | % WRef | W_SF | Point 3 Watts. |  | O
26 | 26 | 1 | RW | Hz4 | Hz4 | uint16 | Hz | Hz_SF | Point 4 Hertz. |  | O
27 | 27 | 1 | RW | W4 | W4 | int16 | % WRef | W_SF | Point 4 Watts. |  | O
28 | 28 | 1 | RW | Hz5 | Hz5 | uint16 | Hz | Hz_SF | Point 5 Hertz. |  | O
29 | 29 | 1 | RW | W5 | W5 | int16 | % WRef | W_SF | Point 5 Watts. |  | O
30 | 30 | 1 | RW | Hz6 | Hz6 | uint16 | Hz | Hz_SF | Point 6 Hertz. |  | O
31 | 31 | 1 | RW | W6 | W6 | int16 | % WRef | W_SF | Point 6 Watts. |  | O
32 | 32 | 1 | RW | Hz7 | Hz7 | uint16 | Hz | Hz_SF | Point 7 Hertz. |  | O
33 | 33 | 1 | RW | W7 | W7 | int16 | % WRef | W_SF | Point 7 Watts. |  | O
34 | 34 | 1 | RW | Hz8 | Hz8 | uint16 | Hz | Hz_SF | Point 8 Hertz. |  | O
35 | 35 | 1 | RW | W8 | W8 | int16 | % WRef | W_SF | Point 8 Watts. |  | O
36 | 36 | 1 | RW | Hz9 | Hz9 | uint16 | Hz | Hz_SF | Point 9 Hertz. |  | O
37 | 37 | 1 | RW | W9 | W9 | int16 | % WRef | W_SF | Point 9 Watts. |  | O
38 | 38 | 1 | RW | Hz10 | Hz10 | uint16 | Hz | Hz_SF | Point 10 Hertz. |  | O
39 | 39 | 1 | RW | W10 | W10 | int16 | % WRef | W_SF | Point 10 Watts. |  | O
40 | 40 | 1 | RW | Hz11 | Hz11 | uint16 | Hz | Hz_SF | Point 11 Hertz. |  | O
41 | 41 | 1 | RW | W11 | W11 | int16 | % WRef | W_SF | Point 11 Watts. |  | O
42 | 42 | 1 | RW | Hz12 | Hz12 | uint16 | Hz | Hz_SF | Point 12 Hertz. |  | O
43 | 43 | 1 | RW | W12 | W12 | int16 | % WRef | W_SF | Point 12 Watts. |  | O
44 | 44 | 1 | RW | Hz13 | Hz13 | uint16 | Hz | Hz_SF | Point 13 Hertz. |  | O
45 | 45 | 1 | RW | W13 | W13 | int16 | % WRef | W_SF | Point 13 Watts. |  | O
46 | 46 | 1 | RW | Hz14 | Hz14 | uint16 | Hz | Hz_SF | Point 14 Hertz. |  | O
47 | 47 | 1 | RW | W14 | W14 | int16 | % WRef | W_SF | Point 14 Watts. |  | O
48 | 48 | 1 | RW | Hz15 | Hz15 | uint16 | Hz | Hz_SF | Point 15 Hertz. |  | O
49 | 49 | 1 | RW | W15 | W15 | int16 | % WRef | W_SF | Point 15 Watts. |  | O
50 | 50 | 1 | RW | Hz16 | Hz16 | uint16 | Hz | Hz_SF | Point 16 Hertz. |  | O
51 | 51 | 1 | RW | W16 | W16 | int16 | % WRef | W_SF | Point 16 Watts. |  | O
52 | 52 | 1 | RW | Hz17 | Hz17 | uint16 | Hz | Hz_SF | Point 17 Hertz. |  | O
53 | 53 | 1 | RW | W17 | W17 | int16 | % WRef | W_SF | Point 17 Watts. |  | O
54 | 54 | 1 | RW | Hz18 | Hz18 | uint16 | Hz | Hz_SF | Point 18 Hertz. |  | O
55 | 55 | 1 | RW | W18 | W18 | int16 | % WRef | W_SF | Point 18 Watts. |  | O
56 | 56 | 1 | RW | Hz19 | Hz19 | uint16 | Hz | Hz_SF | Point 19 Hertz. |  | O
57 | 57 | 1 | RW | W19 | W19 | int16 | % WRef | W_SF | Point 19 Watts. |  | O
58 | 58 | 1 | RW | Hz20 | Hz20 | uint16 | Hz | Hz_SF | Point 20 Hertz. |  | O
59 | 59 | 1 | RW | W20 | W20 | int16 | % WRef | W_SF | Point 20 Watts. |  | O
60 | 67 | 8 | RW | CrvNam | CrvNam | string |  |  | Optional description for curve. (Max 16 chars) |  | O
68 | 68 | 1 | RW | RmpPT1Tms | RmpPT1Tms | uint16 | Secs |  | The time of the PT1 in seconds (time to accomplish a change of 95%). |  | O
69 | 69 | 1 | RW | RmpDecTmm | RmpDecTmm | uint16 | % WMax/min | RmpIncDec_SF | The maximum rate at which the power value may be reduced in response to changes in the frequency value. |  | O
70 | 70 | 1 | RW | RmpIncTmm | RmpIncTmm | uint16 | % WMax/min | RmpIncDec_SF | The maximum rate at which the power value may be increased in response to changes in the frequency value. |  | O
71 | 71 | 1 | R | ReadOnly | ReadOnly | enum16 |  |  | Enumerated value indicates if curve is read-only or can be modified. |  | M
72 | 72 | 1 | R | Pad | Pad | pad |  |  | Pad register. |  | O
// ReadOnly enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
READWRITE |  |  | 0
READONLY |  |  | 1
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0

## IC 135
// 135-LFRT : Low Frequency Ride-through (Ref 4: 11)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 135. Uniquely identifies this as a SunSpec LFRT Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 10+N*50 |  | M
// 135 LFRT Fixed Block (10)
3 | 3 | 1 | RW | ActCrv | ActCrv | uint16 |  |  | Index of active curve. 0=no active curve. |  | M
4 | 4 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | LHzRT control mode. Enable active curve. Bitfield value. |  | M
5 | 5 | 1 | RW | WinTms | WinTms | uint16 | Secs |  | Time window for LFRT change. | Setting is ignored for LFRT controls. | O
6 | 6 | 1 | RW | RvrtTms | RvrtTms | uint16 | Secs |  | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls. | O
7 | 7 | 1 | RW | RmpTms | RmpTms | uint16 | Secs |  | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls. | O
8 | 8 | 1 | R | NCrv | NCrv | uint16 |  |  | Number of curves supported (recommend 4). |  | M
9 | 9 | 1 | R | NPt | NPt | uint16 |  |  | Number of curve points supported (maximumn of 20). |  | M
10 | 10 | 1 | R | Tms_SF | Tms_SF | sunssf |  |  | Scale factor for duration. |  | M
11 | 11 | 1 | R | Hz_SF | Hz_SF | sunssf |  |  | Scale factor for frequency. |  | M
12 | 12 | 1 | R | Pad |  | pad |  |  |  |  | O
// 135 LFRT Repeating Block (50)
13 | 13 | 1 | RW | ActPt | ActPt | uint16 |  |  | Number of active points in array. |  | M
14 | 14 | 1 | RW | Tms1 | Tms1 | uint16 | Secs | Tms_SF | Point 1 must disconnect duration. |  | M
15 | 15 | 1 | RW | Hz1 | Hz1 | uint16 | Hz | Hz_SF | Point 1 must disconnect frequency. |  | M
16 | 16 | 1 | RW | Tms2 | Tms2 | uint16 | Secs | Tms_SF | Point 2 must disconnect duration. |  | O
17 | 17 | 1 | RW | Hz2 | Hz2 | uint16 | Hz | Hz_SF | Point 2 must disconnect frequency. |  | O
18 | 18 | 1 | RW | Tms3 | Tms3 | uint16 | Secs | Tms_SF | Point 3 must disconnect duration. |  | O
19 | 19 | 1 | RW | Hz3 | Hz3 | uint16 | Hz | Hz_SF | Point 3 must disconnect frequency. |  | O
20 | 20 | 1 | RW | Tms4 | Tms4 | uint16 | Secs | Tms_SF | Point 4 must disconnect duration. |  | O
21 | 21 | 1 | RW | Hz4 | Hz4 | uint16 | Hz | Hz_SF | Point 4 must disconnect frequency. |  | O
22 | 22 | 1 | RW | Tms5 | Tms5 | uint16 | Secs | Tms_SF | Point 5 must disconnect duration. |  | O
23 | 23 | 1 | RW | Hz5 | Hz5 | uint16 | Hz | Hz_SF | Point 5 must disconnect frequency. |  | O
24 | 24 | 1 | RW | Tms6 | Tms6 | uint16 | Secs | Tms_SF | Point 6 must disconnect duration. |  | O
25 | 25 | 1 | RW | Hz6 | Hz6 | uint16 | Hz | Hz_SF | Point 6 must disconnect frequency. |  | O
26 | 26 | 1 | RW | Tms7 | Tms7 | uint16 | Secs | Tms_SF | Point 7 must disconnect duration. |  | O
27 | 27 | 1 | RW | Hz7 | Hz7 | uint16 | Hz | Hz_SF | Point 7 must disconnect frequency. |  | O
28 | 28 | 1 | RW | Tms8 | Tms8 | uint16 | Secs | Tms_SF | Point 8 must disconnect duration. |  | O
29 | 29 | 1 | RW | Hz8 | Hz8 | uint16 | Hz | Hz_SF | Point 8 must disconnect frequency. |  | O
30 | 30 | 1 | RW | Tms9 | Tms9 | uint16 | Secs | Tms_SF | Point 9 must disconnect duration. |  | O
31 | 31 | 1 | RW | Hz9 | Hz9 | uint16 | Hz | Hz_SF | Point 9 must disconnect frequency. |  | O
32 | 32 | 1 | RW | Tms10 | Tms10 | uint16 | Secs | Tms_SF | Point 10 must disconnect duration. |  | O
33 | 33 | 1 | RW | Hz10 | Hz10 | uint16 | Hz | Hz_SF | Point 10 must disconnect frequency. |  | O
34 | 34 | 1 | RW | Tms11 | Tms11 | uint16 | Secs | Tms_SF | Point 11 must disconnect duration. |  | O
35 | 35 | 1 | RW | Hz11 | Hz11 | uint16 | Hz | Hz_SF | Point 11 must disconnect frequency. |  | O
36 | 36 | 1 | RW | Tms12 | Tms12 | uint16 | Secs | Tms_SF | Point 12 must disconnect duration. |  | O
37 | 37 | 1 | RW | Hz12 | Hz12 | uint16 | Hz | Hz_SF | Point 12 must disconnect frequency. |  | O
38 | 38 | 1 | RW | Tms13 | Tms13 | uint16 | Secs | Tms_SF | Point 13 must disconnect duration. |  | O
39 | 39 | 1 | RW | Hz13 | Hz13 | uint16 | Hz | Hz_SF | Point 13 must disconnect frequency. |  | O
40 | 40 | 1 | RW | Tms14 | Tms14 | uint16 | Secs | Tms_SF | Point 14 must disconnect duration. |  | O
41 | 41 | 1 | RW | Hz14 | Hz14 | uint16 | Hz | Hz_SF | Point 14 must disconnect frequency. |  | O
42 | 42 | 1 | RW | Tms15 | Tms15 | uint16 | Secs | Tms_SF | Point 15 must disconnect duration. |  | O
43 | 43 | 1 | RW | Hz15 | Hz15 | uint16 | Hz | Hz_SF | Point 15 must disconnect frequency. |  | O
44 | 44 | 1 | RW | Tms16 | Tms16 | uint16 | Secs | Tms_SF | Point 16 must disconnect duration. |  | O
45 | 45 | 1 | RW | Hz16 | Hz16 | uint16 | Hz | Hz_SF | Point 16 must disconnect frequency. |  | O
46 | 46 | 1 | RW | Tms17 | Tms17 | uint16 | Secs | Tms_SF | Point 17 must disconnect duration. |  | O
47 | 47 | 1 | RW | Hz17 | Hz17 | uint16 | Hz | Hz_SF | Point 17 must disconnect frequency. |  | O
48 | 48 | 1 | RW | Tms18 | Tms18 | uint16 | Secs | Tms_SF | Point 18 must disconnect duration. |  | O
49 | 49 | 1 | RW | Hz18 | Hz18 | uint16 | Hz | Hz_SF | Point 18 must disconnect frequency. |  | O
50 | 50 | 1 | RW | Tms19 | Tms19 | uint16 | Secs | Tms_SF | Point 19 must disconnect duration. |  | O
51 | 51 | 1 | RW | Hz19 | Hz19 | uint16 | Hz | Hz_SF | Point 19 must disconnect frequency. |  | O
52 | 52 | 1 | RW | Tms20 | Tms20 | uint16 | Secs | Tms_SF | Point 20 must disconnect duration. |  | O
53 | 53 | 1 | RW | Hz20 | Hz20 | uint16 | Hz | Hz_SF | Point 20 must disconnect frequency. |  | O
54 | 61 | 8 | RW | CrvNam | CrvNam | string |  |  | Optional description for curve. |  | O
62 | 62 | 1 | R | ReadOnly | ReadOnly | enum16 |  |  | Enumerated value indicates if curve is read-only or can be modified. |  | M
// ReadOnly enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
READWRITE |  |  | 0
READONLY |  |  | 1
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0

## IC 136
// 136-HFRT : High Frequency Ride-through (Ref 4: 11)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 136. Uniquely identifies this as a SunSpec HFRT Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 10+N*50 |  | M
// 136 HFRT Fixed Block (10)
3 | 3 | 1 | RW | ActCrv | ActCrv | uint16 |  |  | Index of active curve. 0=no active curve. |  | M
4 | 4 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | HFRT control mode. Enable active curve. Bitfield value. |  | M
5 | 5 | 1 | RW | WinTms | WinTms | uint16 | Secs |  | Time window for HFRT change. | Setting is ignored for HFRT controls. | O
6 | 6 | 1 | RW | RvrtTms | RvrtTms | uint16 | Secs |  | Timeout period for HFRT curve selection. | Setting is ignored for HFRT controls. | O
7 | 7 | 1 | RW | RmpTms | RmpTms | uint16 | Secs |  | Ramp time for moving from current mode to new mode. | Setting is ignored for HFRT controls. | O
8 | 8 | 1 | R | NCrv | NCrv | uint16 |  |  | Number of curves supported (recommend 4). |  | M
9 | 9 | 1 | R | NPt | NPt | uint16 |  |  | Number of curve points supported (maximumn of 20). |  | M
10 | 10 | 1 | R | Tms_SF | Tms_SF | sunssf |  |  | Scale factor for duration. |  | M
11 | 11 | 1 | R | Hz_SF | Hz_SF | sunssf |  |  | Scale factor for frequency. |  | M
12 | 12 | 1 | R | Pad |  | pad |  |  |  |  | O
// 136 HFRT Repeating Block (50)
13 | 13 | 1 | RW | ActPt | ActPt | uint16 |  |  | Number of active points in array. |  | M
14 | 14 | 1 | RW | Tms1 | Tms1 | uint16 | Secs | Tms_SF | Point 1 must disconnect duration. |  | M
15 | 15 | 1 | RW | Hz1 | Hz1 | uint16 | Hz | Hz_SF | Point 1 must disconnect frequency. |  | M
16 | 16 | 1 | RW | Tms2 | Tms2 | uint16 | Secs | Tms_SF | Point 2 must disconnect duration. |  | O
17 | 17 | 1 | RW | Hz2 | Hz2 | uint16 | Hz | Hz_SF | Point 2 must disconnect frequency. |  | O
18 | 18 | 1 | RW | Tms3 | Tms3 | uint16 | Secs | Tms_SF | Point 3 must disconnect duration. |  | O
19 | 19 | 1 | RW | Hz3 | Hz3 | uint16 | Hz | Hz_SF | Point 3 must disconnect frequency. |  | O
20 | 20 | 1 | RW | Tms4 | Tms4 | uint16 | Secs | Tms_SF | Point 4 must disconnect duration. |  | O
21 | 21 | 1 | RW | Hz4 | Hz4 | uint16 | Hz | Hz_SF | Point 4 must disconnect frequency. |  | O
22 | 22 | 1 | RW | Tms5 | Tms5 | uint16 | Secs | Tms_SF | Point 5 must disconnect duration. |  | O
23 | 23 | 1 | RW | Hz5 | Hz5 | uint16 | Hz | Hz_SF | Point 5 must disconnect frequency. |  | O
24 | 24 | 1 | RW | Tms6 | Tms6 | uint16 | Secs | Tms_SF | Point 6 must disconnect duration. |  | O
25 | 25 | 1 | RW | Hz6 | Hz6 | uint16 | Hz | Hz_SF | Point 6 must disconnect frequency. |  | O
26 | 26 | 1 | RW | Tms7 | Tms7 | uint16 | Secs | Tms_SF | Point 7 must disconnect duration. |  | O
27 | 27 | 1 | RW | Hz7 | Hz7 | uint16 | Hz | Hz_SF | Point 7 must disconnect frequency. |  | O
28 | 28 | 1 | RW | Tms8 | Tms8 | uint16 | Secs | Tms_SF | Point 8 must disconnect duration. |  | O
29 | 29 | 1 | RW | Hz8 | Hz8 | uint16 | Hz | Hz_SF | Point 8 must disconnect frequency. |  | O
30 | 30 | 1 | RW | Tms9 | Tms9 | uint16 | Secs | Tms_SF | Point 9 must disconnect duration. |  | O
31 | 31 | 1 | RW | Hz9 | Hz9 | uint16 | Hz | Hz_SF | Point 9 must disconnect frequency. |  | O
32 | 32 | 1 | RW | Tms10 | Tms10 | uint16 | Secs | Tms_SF | Point 10 must disconnect duration. |  | O
33 | 33 | 1 | RW | Hz10 | Hz10 | uint16 | Hz | Hz_SF | Point 10 must disconnect frequency. |  | O
34 | 34 | 1 | RW | Tms11 | Tms11 | uint16 | Secs | Tms_SF | Point 11 must disconnect duration. |  | O
35 | 35 | 1 | RW | Hz11 | Hz11 | uint16 | Hz | Hz_SF | Point 11 must disconnect frequency. |  | O
36 | 36 | 1 | RW | Tms12 | Tms12 | uint16 | Secs | Tms_SF | Point 12 must disconnect duration. |  | O
37 | 37 | 1 | RW | Hz12 | Hz12 | uint16 | Hz | Hz_SF | Point 12 must disconnect frequency. |  | O
38 | 38 | 1 | RW | Tms13 | Tms13 | uint16 | Secs | Tms_SF | Point 13 must disconnect duration. |  | O
39 | 39 | 1 | RW | Hz13 | Hz13 | uint16 | Hz | Hz_SF | Point 13 must disconnect frequency. |  | O
40 | 40 | 1 | RW | Tms14 | Tms14 | uint16 | Secs | Tms_SF | Point 14 must disconnect duration. |  | O
41 | 41 | 1 | RW | Hz14 | Hz14 | uint16 | Hz | Hz_SF | Point 14 must disconnect frequency. |  | O
42 | 42 | 1 | RW | Tms15 | Tms15 | uint16 | Secs | Tms_SF | Point 15 must disconnect duration. |  | O
43 | 43 | 1 | RW | Hz15 | Hz15 | uint16 | Hz | Hz_SF | Point 15 must disconnect frequency. |  | O
44 | 44 | 1 | RW | Tms16 | Tms16 | uint16 | Secs | Tms_SF | Point 16 must disconnect duration. |  | O
45 | 45 | 1 | RW | Hz16 | Hz16 | uint16 | Hz | Hz_SF | Point 16 must disconnect frequency. |  | O
46 | 46 | 1 | RW | Tms17 | Tms17 | uint16 | Secs | Tms_SF | Point 17 must disconnect duration. |  | O
47 | 47 | 1 | RW | Hz17 | Hz17 | uint16 | Hz | Hz_SF | Point 17 must disconnect frequency. |  | O
48 | 48 | 1 | RW | Tms18 | Tms18 | uint16 | Secs | Tms_SF | Point 18 must disconnect duration. |  | O
49 | 49 | 1 | RW | Hz18 | Hz18 | uint16 | Hz | Hz_SF | Point 18 must disconnect frequency. |  | O
50 | 50 | 1 | RW | Tms19 | Tms19 | uint16 | Secs | Tms_SF | Point 19 must disconnect duration. |  | O
51 | 51 | 1 | RW | Hz19 | Hz19 | uint16 | Hz | Hz_SF | Point 19 must disconnect frequency. |  | O
52 | 52 | 1 | RW | Tms20 | Tms20 | uint16 | Secs | Tms_SF | Point 20 must disconnect duration. |  | O
53 | 53 | 1 | RW | Hz20 | Hz20 | uint16 | Hz | Hz_SF | Point 20 must disconnect frequency. |  | O
54 | 61 | 8 | RW | CrvNam | CrvNam | string |  |  | Optional description for curve. |  | O
62 | 62 | 1 | R | ReadOnly | ReadOnly | enum16 |  |  | Enumerated value indicates if curve is read-only or can be modified. |  | M
// ReadOnly enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
READWRITE |  |  | 0
READONLY |  |  | 1
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0

## IC 137
// 137-LVRTC : LVRT must remain connected (Ref 4: 11)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 137. Uniquely identifies this as a SunSpec LVRTC Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 10+N*50 |  | M
// 137 LVRTC Fixed Block (10)
3 | 3 | 1 | RW | ActCrv | ActCrv | uint16 |  |  | Index of active curve. 0=no active curve. |  | M
4 | 4 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | LVRT control mode. Enable active curve. Bitfield value. |  | M
5 | 5 | 1 | RW | WinTms | WinTms | uint16 | Secs |  | Time window for LVRT change. | Setting is ignored for LVRT controls. | O
6 | 6 | 1 | RW | RvrtTms | RvrtTms | uint16 | Secs |  | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls. | O
7 | 7 | 1 | RW | RmpTms | RmpTms | uint16 | Secs |  | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls. | O
8 | 8 | 1 | R | NCrv | NCrv | uint16 |  |  | Number of curves supported (recommend 4). |  | M
9 | 9 | 1 | R | NPt | NPt | uint16 |  |  | Number of curve points supported (maximumn of 20). |  | M
10 | 10 | 1 | R | Tms_SF | Tms_SF | sunssf |  |  | Scale factor for duration. |  | M
11 | 11 | 1 | R | V_SF | V_SF | sunssf |  |  | Scale factor for percent VRef. |  | M
12 | 12 | 1 | R | Pad |  | pad |  |  |  |  | O
// 137 LVRTC Repeating Block (50)
13 | 13 | 1 | RW | ActPt | ActPt | uint16 |  |  | Number of active points in array. |  | M
14 | 14 | 1 | RW | Tms1 | Tms1 | uint16 | Secs | Tms_SF | Point 1 must remain connected duration. |  | M
15 | 15 | 1 | RW | V1 | V1 | uint16 | % VRef | V_SF | Point 1 must remain connected voltage. |  | M
16 | 16 | 1 | RW | Tms2 | Tms2 | uint16 | Secs | Tms_SF | Point 2 must remain connected duration. |  | O
17 | 17 | 1 | RW | V2 | V2 | uint16 | % VRef | V_SF | Point 2 must remain connected voltage. |  | O
18 | 18 | 1 | RW | Tms3 | Tms3 | uint16 | Secs | Tms_SF | Point 3 must remain connected duration. |  | O
19 | 19 | 1 | RW | V3 | V3 | uint16 | % VRef | V_SF | Point 3 must remain connected voltage. |  | O
20 | 20 | 1 | RW | Tms4 | Tms4 | uint16 | Secs | Tms_SF | Point 4 must remain connected duration. |  | O
21 | 21 | 1 | RW | V4 | V4 | uint16 | % VRef | V_SF | Point 4 must remain connected voltage. |  | O
22 | 22 | 1 | RW | Tms5 | Tms5 | uint16 | Secs | Tms_SF | Point 5 must remain connected duration. |  | O
23 | 23 | 1 | RW | V5 | V5 | uint16 | % VRef | V_SF | Point 5 must remain connected voltage. |  | O
24 | 24 | 1 | RW | Tms6 | Tms6 | uint16 | Secs | Tms_SF | Point 6 must remain connected duration. |  | O
25 | 25 | 1 | RW | V6 | V6 | uint16 | % VRef | V_SF | Point 6 must remain connected voltage. |  | O
26 | 26 | 1 | RW | Tms7 | Tms7 | uint16 | Secs | Tms_SF | Point 7 must remain connected duration. |  | O
27 | 27 | 1 | RW | V7 | V7 | uint16 | % VRef | V_SF | Point 7 must remain connected voltage. |  | O
28 | 28 | 1 | RW | Tms8 | Tms8 | uint16 | Secs | Tms_SF | Point 8 must remain connected duration. |  | O
29 | 29 | 1 | RW | V8 | V8 | uint16 | % VRef | V_SF | Point 8 must remain connected voltage. |  | O
30 | 30 | 1 | RW | Tms9 | Tms9 | uint16 | Secs | Tms_SF | Point 9 must remain connected duration. |  | O
31 | 31 | 1 | RW | V9 | V9 | uint16 | % VRef | V_SF | Point 9 must remain connected voltage. |  | O
32 | 32 | 1 | RW | Tms10 | Tms10 | uint16 | Secs | Tms_SF | Point 10 must remain connected duration. |  | O
33 | 33 | 1 | RW | V10 | V10 | uint16 | % VRef | V_SF | Point 10 must remain connected voltage. |  | O
34 | 34 | 1 | RW | Tms11 | Tms11 | uint16 | Secs | Tms_SF | Point 11 must remain connected duration. |  | O
35 | 35 | 1 | RW | V11 | V11 | uint16 | % VRef | V_SF | Point 11 must remain connected voltage. |  | O
36 | 36 | 1 | RW | Tms12 | Tms12 | uint16 | Secs | Tms_SF | Point 12 must remain connected duration. |  | O
37 | 37 | 1 | RW | V12 | V12 | uint16 | % VRef | V_SF | Point 12 must remain connected voltage. |  | O
38 | 38 | 1 | RW | Tms13 | Tms13 | uint16 | Secs | Tms_SF | Point 13 must remain connected duration. |  | O
39 | 39 | 1 | RW | V13 | V13 | uint16 | % VRef | V_SF | Point 13 must remain connected voltage. |  | O
40 | 40 | 1 | RW | Tms14 | Tms14 | uint16 | Secs | Tms_SF | Point 14 must remain connected duration. |  | O
41 | 41 | 1 | RW | V14 | V14 | uint16 | % VRef | V_SF | Point 14 must remain connected voltage. |  | O
42 | 42 | 1 | RW | Tms15 | Tms15 | uint16 | Secs | Tms_SF | Point 15 must remain connected duration. |  | O
43 | 43 | 1 | RW | V15 | V15 | uint16 | % VRef | V_SF | Point 15 must remain connected voltage. |  | O
44 | 44 | 1 | RW | Tms16 | Tms16 | uint16 | Secs | Tms_SF | Point 16 must remain connected duration. |  | O
45 | 45 | 1 | RW | V16 | V16 | uint16 | % VRef | V_SF | Point 16 must remain connected voltage. |  | O
46 | 46 | 1 | RW | Tms17 | Tms17 | uint16 | Secs | Tms_SF | Point 17 must remain connected duration. |  | O
47 | 47 | 1 | RW | V17 | V17 | uint16 | % VRef | V_SF | Point 17 must remain connected voltage. |  | O
48 | 48 | 1 | RW | Tms18 | Tms18 | uint16 | Secs | Tms_SF | Point 18 must remain connected duration. |  | O
49 | 49 | 1 | RW | V18 | V18 | uint16 | % VRef | V_SF | Point 18 must remain connected voltage. |  | O
50 | 50 | 1 | RW | Tms19 | Tms19 | uint16 | Secs | Tms_SF | Point 19 must remain connected duration. |  | O
51 | 51 | 1 | RW | V19 | V19 | uint16 | % VRef | V_SF | Point 19 must remain connected voltage. |  | O
52 | 52 | 1 | RW | Tms20 | Tms20 | uint16 | Secs | Tms_SF | Point 20 must remain connected duration. |  | O
53 | 53 | 1 | RW | V20 | V20 | uint16 | % VRef | V_SF | Point 20 must remain connected voltage. |  | O
54 | 61 | 8 | RW | CrvNam | CrvNam | string |  |  | Optional description for curve. |  | O
62 | 62 | 1 | R | ReadOnly | ReadOnly | enum16 |  |  | Enumerated value indicates if curve is read-only or can be modified. |  | M
// ReadOnly enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
READWRITE |  |  | 0
READONLY |  |  | 1
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0

## IC 138
// 138-HVRTC : HVRT must remain connected (Ref 4: 11)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 138. Uniquely identifies this as a SunSpec HVRTC Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 10+N*50 |  | M
// 138 HVRTC Fixed Block (10)
3 | 3 | 1 | RW | ActCrv | ActCrv | uint16 |  |  | Index of active curve. 0=no active curve. |  | M
4 | 4 | 1 | RW | ModEna | ModEna | bitfield16 |  |  | HVRT control mode. Enable active curve. Bitfield value. |  | M
5 | 5 | 1 | RW | WinTms | WinTms | uint16 | Secs |  | Time window for HVRT change. | Setting is ignored for HVRT controls. | O
6 | 6 | 1 | RW | RvrtTms | RvrtTms | uint16 | Secs |  | Timeout period for HVRT curve selection. | Setting is ignored for HVRT controls. | O
7 | 7 | 1 | RW | RmpTms | RmpTms | uint16 | Secs |  | Ramp time for moving from current mode to new mode. | Setting is ignored for HVRT controls. | O
8 | 8 | 1 | R | NCrv | NCrv | uint16 |  |  | Number of curves supported (recommend 4). |  | M
9 | 9 | 1 | R | NPt | NPt | uint16 |  |  | Number of curve points supported (maximumn of 20). |  | M
10 | 10 | 1 | R | Tms_SF | Tms_SF | sunssf |  |  | Scale factor for duration. |  | M
11 | 11 | 1 | R | V_SF | V_SF | sunssf |  |  | Scale factor for percent VRef. |  | M
12 | 12 | 1 | R | Pad |  | pad |  |  |  |  | O
// 138 HVRTC Repeating Block (50)
13 | 13 | 1 | RW | ActPt | ActPt | uint16 |  |  | Number of active points in array. |  | M
14 | 14 | 1 | RW | Tms1 | Tms1 | uint16 | Secs | Tms_SF | Point 1 must remain connected duration. |  | M
15 | 15 | 1 | RW | V1 | V1 | uint16 | % VRef | V_SF | Point 1 must remain connected voltage. |  | M
16 | 16 | 1 | RW | Tms2 | Tms2 | uint16 | Secs | Tms_SF | Point 2 must remain connected duration. |  | O
17 | 17 | 1 | RW | V2 | V2 | uint16 | % VRef | V_SF | Point 2 must remain connected voltage. |  | O
18 | 18 | 1 | RW | Tms3 | Tms3 | uint16 | Secs | Tms_SF | Point 3 must remain connected duration. |  | O
19 | 19 | 1 | RW | V3 | V3 | uint16 | % VRef | V_SF | Point 3 must remain connected voltage. |  | O
20 | 20 | 1 | RW | Tms4 | Tms4 | uint16 | Secs | Tms_SF | Point 4 must remain connected duration. |  | O
21 | 21 | 1 | RW | V4 | V4 | uint16 | % VRef | V_SF | Point 4 must remain connected voltage. |  | O
22 | 22 | 1 | RW | Tms5 | Tms5 | uint16 | Secs | Tms_SF | Point 5 must remain connected duration. |  | O
23 | 23 | 1 | RW | V5 | V5 | uint16 | % VRef | V_SF | Point 5 must remain connected voltage. |  | O
24 | 24 | 1 | RW | Tms6 | Tms6 | uint16 | Secs | Tms_SF | Point 6 must remain connected duration. |  | O
25 | 25 | 1 | RW | V6 | V6 | uint16 | % VRef | V_SF | Point 6 must remain connected voltage. |  | O
26 | 26 | 1 | RW | Tms7 | Tms7 | uint16 | Secs | Tms_SF | Point 7 must remain connected duration. |  | O
27 | 27 | 1 | RW | V7 | V7 | uint16 | % VRef | V_SF | Point 7 must remain connected voltage. |  | O
28 | 28 | 1 | RW | Tms8 | Tms8 | uint16 | Secs | Tms_SF | Point 8 must remain connected duration. |  | O
29 | 29 | 1 | RW | V8 | V8 | uint16 | % VRef | V_SF | Point 8 must remain connected voltage. |  | O
30 | 30 | 1 | RW | Tms9 | Tms9 | uint16 | Secs | Tms_SF | Point 9 must remain connected duration. |  | O
31 | 31 | 1 | RW | V9 | V9 | uint16 | % VRef | V_SF | Point 9 must remain connected voltage. |  | O
32 | 32 | 1 | RW | Tms10 | Tms10 | uint16 | Secs | Tms_SF | Point 10 must remain connected duration. |  | O
33 | 33 | 1 | RW | V10 | V10 | uint16 | % VRef | V_SF | Point 10 must remain connected voltage. |  | O
34 | 34 | 1 | RW | Tms11 | Tms11 | uint16 | Secs | Tms_SF | Point 11 must remain connected duration. |  | O
35 | 35 | 1 | RW | V11 | V11 | uint16 | % VRef | V_SF | Point 11 must remain connected voltage. |  | O
36 | 36 | 1 | RW | Tms12 | Tms12 | uint16 | Secs | Tms_SF | Point 12 must remain connected duration. |  | O
37 | 37 | 1 | RW | V12 | V12 | uint16 | % VRef | V_SF | Point 12 must remain connected voltage. |  | O
38 | 38 | 1 | RW | Tms13 | Tms13 | uint16 | Secs | Tms_SF | Point 13 must remain connected duration. |  | O
39 | 39 | 1 | RW | V13 | V13 | uint16 | % VRef | V_SF | Point 13 must remain connected voltage. |  | O
40 | 40 | 1 | RW | Tms14 | Tms14 | uint16 | Secs | Tms_SF | Point 14 must remain connected duration. |  | O
41 | 41 | 1 | RW | V14 | V14 | uint16 | % VRef | V_SF | Point 14 must remain connected voltage. |  | O
42 | 42 | 1 | RW | Tms15 | Tms15 | uint16 | Secs | Tms_SF | Point 15 must remain connected duration. |  | O
43 | 43 | 1 | RW | V15 | V15 | uint16 | % VRef | V_SF | Point 15 must remain connected voltage. |  | O
44 | 44 | 1 | RW | Tms16 | Tms16 | uint16 | Secs | Tms_SF | Point 16 must remain connected duration. |  | O
45 | 45 | 1 | RW | V16 | V16 | uint16 | % VRef | V_SF | Point 16 must remain connected voltage. |  | O
46 | 46 | 1 | RW | Tms17 | Tms17 | uint16 | Secs | Tms_SF | Point 17 must remain connected duration. |  | O
47 | 47 | 1 | RW | V17 | V17 | uint16 | % VRef | V_SF | Point 17 must remain connected voltage. |  | O
48 | 48 | 1 | RW | Tms18 | Tms18 | uint16 | Secs | Tms_SF | Point 18 must remain connected duration. |  | O
49 | 49 | 1 | RW | V18 | V18 | uint16 | % VRef | V_SF | Point 18 must remain connected voltage. |  | O
50 | 50 | 1 | RW | Tms19 | Tms19 | uint16 | Secs | Tms_SF | Point 19 must remain connected duration. |  | O
51 | 51 | 1 | RW | V19 | V19 | uint16 | % VRef | V_SF | Point 19 must remain connected voltage. |  | O
52 | 52 | 1 | RW | Tms20 | Tms20 | uint16 | Secs | Tms_SF | Point 20 must remain connected duration. |  | O
53 | 53 | 1 | RW | V20 | V20 | uint16 | % VRef | V_SF | Point 20 must remain connected voltage. |  | O
54 | 61 | 8 | RW | CrvNam | CrvNam | string |  |  | Optional description for curve. |  | O
62 | 62 | 1 | R | ReadOnly | ReadOnly | enum16 |  |  | Enumerated value indicates if curve is read-only or can be modified. |  | M
// ReadOnly enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
READWRITE |  |  | 0
READONLY |  |  | 1
// ModEna bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ENABLED |  |  | 0

## I 160
// 160-Multiple MPPT Inverter Extension Model : ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID | Input ID | unit16 |  |  | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 8+N*20 |  | M
// 160 Multiple MPPT Inverter Extension Model Fixed Block (8)
3 | 3 | 1 | R | DCA_SF | Current Scale Factor | sunssf |  |  |  |  | O
4 | 4 | 1 | R | DCV_SF | Voltage Scale Factor | sunssf |  |  |  |  | O
5 | 5 | 1 | R | DCW_SF | Power Scale Factor | sunssf |  |  |  |  | O
6 | 6 | 1 | R | DCWH_SF | Energy Scale Factor | sunssf |  |  |  |  | O
7 | 8 | 2 | R | Evt | Global Events | bitfield32 |  |  |  |  | O
9 | 9 | 1 | R | N | Number of Modules | uint16 |  |  |  |  | O
10 | 10 | 1 | R | TmsPer | Timestamp Period | uint16 |  |  |  |  | O
// 160 Multiple MPPT Inverter Extension Model Repeating Block (20)
11 | 11 | 1 | R | ID | Input ID | uint16 |  |  |  |  | O
12 | 19 | 8 | R | IDStr | Input ID Sting | string |  |  |  |  | O
20 | 20 | 1 | R | DCA | DC Current | uint16 |  |  |  |  | O
21 | 21 | 1 | R | DCV | DC Voltage | uint16 |  |  |  |  | O
22 | 22 | 1 | R | DCW | DC Power | uint16 |  |  |  |  | O
23 | 24 | 2 | R | DCWH | Lifetime Energy | acc32 |  |  |  |  | O
25 | 26 | 2 | R | Tms | Timestamp | uint32 | Secs |  |  |  | O
27 | 27 | 1 | R | Tmp | Temperature | int16 |  |  |  |  | O
28 | 28 | 1 | R | DCSt | Operating State | enum16 |  |  |  |  | O
29 | 30 | 2 | R | DCEvt | Module Events | bitfield32 |  |  |  |  | O
// DCSt enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
OFF |  |  | 1 |  | Off
SLEEPING |  |  | 2 |  | Sleeping
STARTING |  |  | 3 |  | Starting
MPPT |  |  | 4 |  | MPPT
THROTTLED |  |  | 5 |  | Throttled
SHUTTING_DOWN |  |  | 6 |  | Shutting Down
FAULT |  |  | 7 |  | Fault
STANDBY |  |  | 8 |  | Standby
TEST |  |  | 9 |  | Test
RESERVED |  |  | 10 |  | Reserved
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
GROUND_FAULT |  |  | 0 |  | Ground Fault
INPUT_OVER_VOLTAGE |  |  | 1 |  | Input Over Voltage
RESERVED |  |  | 2 |  | Reserved
DC_DISCONNECT |  |  | 3 |  | DC Disconnect
RESERVED |  |  | 4 |  | Reserved
CABINET_OPEN |  |  | 5 |  | Cabinet Open
MANUAL_SHUTDOWN |  |  | 6 |  | Manual Shutdown
OVER_TEMP |  |  | 7 |  | Over Temperature
RESERVED |  |  | 8 |  | Reserved
RESERVED |  |  | 9 |  | Reserved
RESERVED |  |  | 10 |  | Reserved
RESERVED |  |  | 11 |  | Reserved
BLOWN_FUSE |  |  | 12 |  | Blown Fuse
UNDER_TEMP |  |  | 13 |  | Under Temperature
MEMORY_LOSS |  |  | 14 |  | Memory Loss
ARC_DETECTION |  |  | 15 |  | Arc Detection
RESERVED |  |  | 16 |  | Reserved
RESERVED |  |  | 17 |  | Reserved
RESERVED |  |  | 18 |  | Reserved
RESERVED |  |  | 19 |  | Reserved
TEST_FAILED |  |  | 20 |  | Test Failed
INPUT_UNDER_VOLTAGE |  |  | 21 |  | Under Voltage
INPUT_OVER_CURRENT |  |  | 22 |  | Over Current
// DCEvt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
GROUND_FAULT |  |  | 0 |  | Ground Fault
INPUT_OVER_VOLTAGE |  |  | 1 |  | Input Over Voltage
RESERVED |  |  | 2 |  | Reserved
DC_DISCONNECT |  |  | 3 |  | DC Disconnect
RESERVED |  |  | 4 |  | Reserved
CABINET_OPEN |  |  | 5 |  | Cabinet Open
MANUAL_SHUTDOWN |  |  | 6 |  | Manual Shutdown
OVER_TEMP |  |  | 7 |  | Over Temperature
RESERVED |  |  | 8 |  | Reserved
RESERVED |  |  | 9 |  | Reserved
RESERVED |  |  | 10 |  | Reserved
RESERVED |  |  | 11 |  | Reserved
BLOWN_FUSE |  |  | 12 |  | Blown Fuse
UNDER_TEMP |  |  | 13 |  | Under Temperature
MEMORY_LOSS |  |  | 14 |  | Memory Loss
ARC_DETECTION |  |  | 15 |  | Arc Detection
RESERVED |  |  | 16 |  | Reserved
RESERVED |  |  | 17 |  | Reserved
RESERVED |  |  | 18 |  | Reserved
RESERVED |  |  | 19 |  | Reserved
TEST_FAILED |  |  | 20 |  | Test Failed
INPUT_UNDER_VOLTAGE |  |  | 21 |  | Under Voltage
INPUT_OVER_CURRENT |  |  | 22 |  | Over Current

## M 201
// 201-Meter (Single Phase)single phase (AN or AB) meter : Include this model for single phase (AN or AB) metering ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 201. Uniquely identifies this as a SunSpec Meter (Single Phase)single phase (AN or AB) meter Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 105 |  | M
// 201 Meter (Single Phase)single phase (AN or AB) meter Fixed Block (105)
3 | 3 | 1 | R | A | Amps | int16 | A | A_SF | Total AC Current |  | M
4 | 4 | 1 | R | AphA | Amps PhaseA | int16 | A | A_SF | Phase A Current |  | M
5 | 5 | 1 | R | AphB | Amps PhaseB | int16 | A | A_SF | Phase B Current |  | O
6 | 6 | 1 | R | AphC | Amps PhaseC | int16 | A | A_SF | Phase C Current |  | O
7 | 7 | 1 | R | A_SF |  | sunssf |  |  | Current scale factor |  | M
8 | 8 | 1 | R | PhV | Voltage LN | int16 | V | V_SF | Line to Neutral AC Voltage (average of active phases) | Conditional AN connection | O
9 | 9 | 1 | R | PhVphA | Phase Voltage AN | int16 | V | V_SF | Phase Voltage AN | Conditional AN connection | O
10 | 10 | 1 | R | PhVphB | Phase Voltage BN | int16 | V | V_SF | Phase Voltage BN |  | O
11 | 11 | 1 | R | PhVphC | Phase Voltage CN | int16 | V | V_SF | Phase Voltage CN |  | O
12 | 12 | 1 | R | PPV | Voltage LL | int16 | V | V_SF | Line to Line AC Voltage (average of active phases) |  | O
13 | 13 | 1 | R | PPVphAB | Phase Voltage AB | int16 | V | V_SF | Phase Voltage AB | Conditional AB connection | O
14 | 14 | 1 | R | PPVphBC | Phase Voltage BC | int16 | V | V_SF | Phase Voltage BC |  | O
15 | 15 | 1 | R | PPVphCA | Phase Voltage CA | int16 | V | V_SF | Phase Voltage CA |  | O
16 | 16 | 1 | R | V_SF |  | sunssf |  |  | Voltage scale factor |  | M
17 | 17 | 1 | R | Hz | Hz | int16 | Hz | Hz_SF | Frequency |  | M
18 | 18 | 1 | R | Hz_SF |  | sunssf |  |  | Frequency scale factor |  | O
19 | 19 | 1 | R | W | Watts | int16 | W | W_SF | Total Real Power |  | M
20 | 20 | 1 | R | WphA | Watts phase A | int16 | W | W_SF |  |  | O
21 | 21 | 1 | R | WphB | Watts phase B | int16 | W | W_SF |  |  | O
22 | 22 | 1 | R | WphC | Watts phase C | int16 | W | W_SF |  |  | O
23 | 23 | 1 | R | W_SF |  | sunssf |  |  | Real Power scale factor |  | M
24 | 24 | 1 | R | VA | VA | int16 | VA | VA_SF | AC Apparent Power |  | O
25 | 25 | 1 | R | VAphA | VA phase A | int16 | VA | VA_SF |  |  | O
26 | 26 | 1 | R | VAphB | VA phase B | int16 | VA | VA_SF |  |  | O
27 | 27 | 1 | R | VAphC | VA phase C | int16 | VA | VA_SF |  |  | O
28 | 28 | 1 | R | VA_SF |  | sunssf |  |  | Apparent Power scale factor |  | O
29 | 29 | 1 | R | VAR | VAR | int16 | var | VAR_SF | Reactive Power |  | O
30 | 30 | 1 | R | VARphA | VAR phase A | int16 | var | VAR_SF |  |  | O
31 | 31 | 1 | R | VARphB | VAR phase B | int16 | var | VAR_SF |  |  | O
32 | 32 | 1 | R | VARphC | VAR phase C | int16 | var | VAR_SF |  |  | O
33 | 33 | 1 | R | VAR_SF |  | sunssf |  |  | Reactive Power scale factor |  | O
34 | 34 | 1 | R | PF | PF | int16 | Pct | PF_SF | Power Factor |  | O
35 | 35 | 1 | R | PFphA | PF phase A | int16 | Pct | PF_SF |  |  | O
36 | 36 | 1 | R | PFphB | PF phase B | int16 | Pct | PF_SF |  |  | O
37 | 37 | 1 | R | PFphC | PF phase C | int16 | Pct | PF_SF |  |  | O
38 | 38 | 1 | R | PF_SF |  | sunssf |  |  | Power Factor scale factor |  | O
39 | 40 | 2 | R | TotWhExp | Total Watt-hours Exported | acc32 | Wh | TotWh_SF | Total Real Energy Exported |  | M
41 | 42 | 2 | R | TotWhExpPhA | Total Watt-hours Exported phase A | acc32 | Wh | TotWh_SF |  |  | O
43 | 44 | 2 | R | TotWhExpPhB | Total Watt-hours Exported phase B | acc32 | Wh | TotWh_SF |  |  | O
45 | 46 | 2 | R | TotWhExpPhC | Total Watt-hours Exported phase C | acc32 | Wh | TotWh_SF |  |  | O
47 | 48 | 2 | R | TotWhImp | Total Watt-hours Imported | acc32 | Wh | TotWh_SF | Total Real Energy Imported |  | M
49 | 50 | 2 | R | TotWhImpPhA | Total Watt-hours Imported phase A | acc32 | Wh | TotWh_SF |  |  | O
51 | 52 | 2 | R | TotWhImpPhB | Total Watt-hours Imported phase B | acc32 | Wh | TotWh_SF |  |  | O
53 | 54 | 2 | R | TotWhImpPhC | Total Watt-hours Imported phase C | acc32 | Wh | TotWh_SF |  |  | O
55 | 55 | 1 | R | TotWh_SF |  | sunssf |  |  | Real Energy scale factor |  | M
56 | 57 | 2 | R | TotVAhExp | Total VA-hours Exported | acc32 | VAh | TotVAh_SF | Total Apparent Energy Exported |  | O
58 | 59 | 2 | R | TotVAhExpPhA | Total VA-hours Exported phase A | acc32 | VAh | TotVAh_SF |  |  | O
60 | 61 | 2 | R | TotVAhExpPhB | Total VA-hours Exported phase B | acc32 | VAh | TotVAh_SF |  |  | O
62 | 63 | 2 | R | TotVAhExpPhC | Total VA-hours Exported phase C | acc32 | VAh | TotVAh_SF |  |  | O
64 | 65 | 2 | R | TotVAhImp | Total VA-hours Imported | acc32 | VAh | TotVAh_SF | Total Apparent Energy Imported |  | O
66 | 67 | 2 | R | TotVAhImpPhA | Total VA-hours Imported phase A | acc32 | VAh | TotVAh_SF |  |  | O
68 | 69 | 2 | R | TotVAhImpPhB | Total VA-hours Imported phase B | acc32 | VAh | TotVAh_SF |  |  | O
70 | 71 | 2 | R | TotVAhImpPhC | Total VA-hours Imported phase C | acc32 | VAh | TotVAh_SF |  |  | O
72 | 72 | 1 | R | TotVAh_SF |  | sunssf |  |  | Apparent Energy scale factor |  | O
73 | 74 | 2 | R | TotVArhImpQ1 | Total VAR-hours Imported Q1 | acc32 | varh | TotVArh_SF | Total Reactive Energy Imported Quadrant 1 |  | O
75 | 76 | 2 | R | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A | acc32 | varh | TotVArh_SF |  |  | O
77 | 78 | 2 | R | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B | acc32 | varh | TotVArh_SF |  |  | O
79 | 80 | 2 | R | TotVArhImpQ1PhC | Total VAr-hourse Imported Q1 phase C | acc32 | varh | TotVArh_SF |  |  | O
81 | 82 | 2 | R | TotVArhImpQ2 | Total VAr-hours Imported Q2 | acc32 | varh | TotVArh_SF | Total Reactive Power Imported Quadrant 2 |  | O
83 | 84 | 2 | R | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A | acc32 | varh | TotVArh_SF |  |  | O
85 | 86 | 2 | R | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B | acc32 | varh | TotVArh_SF |  |  | O
87 | 88 | 2 | R | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C | acc32 | varh | TotVArh_SF |  |  | O
89 | 90 | 2 | R | TotVArhExpQ3 | Total VAr-hours Exported Q3 | acc32 | varh | TotVArh_SF | Total Reactive Power Exported Quadrant 3 |  | O
91 | 92 | 2 | R | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A | acc32 | varh | TotVArh_SF |  |  | O
93 | 94 | 2 | R | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B | acc32 | varh | TotVArh_SF |  |  | O
95 | 96 | 2 | R | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C | acc32 | varh | TotVArh_SF |  |  | O
97 | 98 | 2 | R | TotVArhExpQ4 | Total VAr-hours Exported Q4 | acc32 | varh | TotVArh_SF | Total Reactive Power Exported Quadrant 4 |  | O
99 | 100 | 2 | R | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A | acc32 | varh | TotVArh_SF |  |  | O
101 | 102 | 2 | R | TotVArhExpQ4PhB |  | acc32 | varh | TotVArh_SF |  |  | O
103 | 104 | 2 | R | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C | acc32 | varh | TotVArh_SF |  |  | O
105 | 105 | 1 | R | TotVArh_SF |  | sunssf |  |  | Reactive Energy scale factor |  | O
106 | 107 | 2 | R | Evt | Events | bitfield32 |  |  | Meter Event Flags |  | M
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Power_Failure |  |  | 2 |  | Power Failure |  | Loss of power or phase
Under_Voltage |  |  | 3 |  | Under Voltage |  | Voltage below threshold (Phase Loss)
Low_PF |  |  | 4 |  | Low PF |  | Power Factor below threshold
Over_Current |  |  | 5 |  | Over Current |  | Current Input over threshold
Over_Voltage |  |  | 6 |  | Over Voltage |  | Voltage Input over threshold
Missing_Sensor |  |  | 7 |  | Missing Sensor |  | Sensor not connected
OEM01 |  |  | 16 |  | OEM01 |  | Reserved for OEM use
OEM02 |  |  | 17 |  | OEM02 |  | Reserved for OEM use
OEM03 |  |  | 18 |  | OEM01 |  | Reserved for OEM use
OEM04 |  |  | 19 |  | OEM04 |  | Reserved for OEM use
OEM05 |  |  | 20 |  | OEM05 |  | Reserved for OEM use
OEM06 |  |  | 21 |  | OEM06 |  | Reserved for OEM use
OEM07 |  |  | 22 |  | OEM07 |  | Reserved for OEM use
OEM08 |  |  | 23 |  | OEM08 |  | Reserved for OEM use
OEM09 |  |  | 24 |  | OEM09 |  | Reserved for OEM use
OEM10 |  |  | 25 |  | OEM10 |  | Reserved for OEM use
OEM11 |  |  | 26 |  | OEM11 |  | Reserved for OEM use
OEM12 |  |  | 27 |  | OEM12 |  | Reserved for OEM use
OEM13 |  |  | 28 |  | OEM13 |  | Reserved for OEM use
OEM14 |  |  | 29 |  | OEM14 |  | Reserved for OEM use
OEM15 |  |  | 30 |  | OEM15 |  | Reserved for OEM use

## M 202
// 202-split single phase (ABN) meter : ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 202. Uniquely identifies this as a SunSpec split single phase (ABN) meter Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 105 |  | M
// 202 split single phase (ABN) meter Fixed Block (105)
3 | 3 | 1 | R | A | Amps | int16 | A | A_SF | Total AC Current |  | M
4 | 4 | 1 | R | AphA | Amps PhaseA | int16 | A | A_SF | Phase A Current |  | O
5 | 5 | 1 | R | AphB | Amps PhaseB | int16 | A | A_SF | Phase B Current |  | M
6 | 6 | 1 | R | AphC | Amps PhaseC | int16 | A | A_SF | Phase C Current |  | M
7 | 7 | 1 | R | A_SF |  | sunssf |  |  | Current scale factor |  | M
8 | 8 | 1 | R | PhV | Voltage LN | int16 | V | V_SF | Line to Neutral AC Voltage (average of active phases) |  | M
9 | 9 | 1 | R | PhVphA | Phase Voltage AN | int16 | V | V_SF | Phase Voltage AN |  | M
10 | 10 | 1 | R | PhVphB | Phase Voltage BN | int16 | V | V_SF | Phase Voltage BN |  | M
11 | 11 | 1 | R | PhVphC | Phase Voltage CN | int16 | V | V_SF | Phase Voltage CN |  | O
12 | 12 | 1 | R | PPV | Voltage LL | int16 | V | V_SF | Line to Line AC Voltage (average of active phases) |  | M
13 | 13 | 1 | R | PhVphAB |  | int16 | V | V_SF |  |  | M
14 | 14 | 1 | R | PhVphBC |  | int16 | V | V_SF |  |  | O
15 | 15 | 1 | R | PhVphCA |  | int16 | V | V_SF |  |  | O
16 | 16 | 1 | R | V_SF |  | sunssf |  |  | Voltage scale factor |  | M
17 | 17 | 1 | R | Hz | Hz | int16 | Hz | Hz_SF | Frequency |  | M
18 | 18 | 1 | R | Hz_SF |  | sunssf |  |  | Frequency scale factor |  | O
19 | 19 | 1 | R | W | Watts | int16 | W | W_SF | Total Real Power |  | M
20 | 20 | 1 | R | WphA | Watts phase A | int16 | W | W_SF |  |  | O
21 | 21 | 1 | R | WphB | Watts phase B | int16 | W | W_SF |  |  | O
22 | 22 | 1 | R | WphC | Watts phase C | int16 | W | W_SF |  |  | O
23 | 23 | 1 | R | W_SF |  | sunssf |  |  | Real Power scale factor |  | M
24 | 24 | 1 | R | VA | VA | int16 | VA | VA_SF | AC Apparent Power |  | O
25 | 25 | 1 | R | VAphA | VA phase A | int16 | VA | VA_SF |  |  | O
26 | 26 | 1 | R | VAphB | VA phase B | int16 | VA | VA_SF |  |  | O
27 | 27 | 1 | R | VAphC | VA phase C | int16 | VA | VA_SF |  |  | O
28 | 28 | 1 | R | VA_SF |  | sunssf |  |  | Apparent Power scale factor |  | O
29 | 29 | 1 | R | VAR | VAR | int16 | var | VAR_SF | Reactive Power |  | O
30 | 30 | 1 | R | VARphA | VAR phase A | int16 | var | VAR_SF |  |  | O
31 | 31 | 1 | R | VARphB | VAR phase B | int16 | var | VAR_SF |  |  | O
32 | 32 | 1 | R | VARphC | VAR phase C | int16 | var | VAR_SF |  |  | O
33 | 33 | 1 | R | VAR_SF |  | sunssf |  |  | Reactive Power scale factor |  | O
34 | 34 | 1 | R | PF | PF | int16 | Pct | PF_SF | Power Factor |  | O
35 | 35 | 1 | R | PFphA | PF phase A | int16 | Pct | PF_SF |  |  | O
36 | 36 | 1 | R | PFphB | PF phase B | int16 | Pct | PF_SF |  |  | O
37 | 37 | 1 | R | PFphC | PF phase C | int16 | Pct | PF_SF |  |  | O
38 | 38 | 1 | R | PF_SF |  | sunssf |  |  | Power Factor scale factor |  | O
39 | 40 | 2 | R | TotWhExp | Total Watt-hours Exported | acc32 | Wh | TotWh_SF | Total Real Energy Exported |  | M
41 | 42 | 2 | R | TotWhExpPhA | Total Watt-hours Exported phase A | acc32 | Wh | TotWh_SF |  |  | O
43 | 44 | 2 | R | TotWhExpPhB | Total Watt-hours Exported phase B | acc32 | Wh | TotWh_SF |  |  | O
45 | 46 | 2 | R | TotWhExpPhC | Total Watt-hours Exported phase C | acc32 | Wh | TotWh_SF |  |  | O
47 | 48 | 2 | R | TotWhImp | Total Watt-hours Imported | acc32 | Wh | TotWh_SF | Total Real Energy Imported |  | M
49 | 50 | 2 | R | TotWhImpPhA | Total Watt-hours Imported phase A | acc32 | Wh | TotWh_SF |  |  | O
51 | 52 | 2 | R | TotWhImpPhB | Total Watt-hours Imported phase B | acc32 | Wh | TotWh_SF |  |  | O
53 | 54 | 2 | R | TotWhImpPhC | Total Watt-hours Imported phase C | acc32 | Wh | TotWh_SF |  |  | O
55 | 55 | 1 | R | TotWh_SF |  | sunssf |  |  | Real Energy scale factor |  | M
56 | 57 | 2 | R | TotVAhExp | Total VA-hours Exported | acc32 | VAh | TotVAh_SF | Total Apparent Energy Exported |  | O
58 | 59 | 2 | R | TotVAhExpPhA | Total VA-hours Exported phase A | acc32 | VAh | TotVAh_SF |  |  | O
60 | 61 | 2 | R | TotVAhExpPhB | Total VA-hours Exported phase B | acc32 | VAh | TotVAh_SF |  |  | O
62 | 63 | 2 | R | TotVAhExpPhC | Total VA-hours Exported phase C | acc32 | VAh | TotVAh_SF |  |  | O
64 | 65 | 2 | R | TotVAhImp | Total VA-hours Imported | acc32 | VAh | TotVAh_SF | Total Apparent Energy Imported |  | O
66 | 67 | 2 | R | TotVAhImpPhA | Total VA-hours Imported phase A | acc32 | VAh | TotVAh_SF |  |  | O
68 | 69 | 2 | R | TotVAhImpPhB | Total VA-hours Imported phase B | acc32 | VAh | TotVAh_SF |  |  | O
70 | 71 | 2 | R | TotVAhImpPhC | Total VA-hours Imported phase C | acc32 | VAh | TotVAh_SF |  |  | O
72 | 72 | 1 | R | TotVAh_SF |  | sunssf |  |  | Apparent Energy scale factor |  | O
73 | 74 | 2 | R | TotVArhImpQ1 | Total VAR-hours Imported Q1 | acc32 | varh | TotVArh_SF | Total Reactive Energy Imported Quadrant 1 |  | O
75 | 76 | 2 | R | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A | acc32 | varh | TotVArh_SF |  |  | O
77 | 78 | 2 | R | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B | acc32 | varh | TotVArh_SF |  |  | O
79 | 80 | 2 | R | TotVArhImpQ1PhC | Total VAr-hourse Imported Q1 phase C | acc32 | varh | TotVArh_SF |  |  | O
81 | 82 | 2 | R | TotVArhImpQ2 | Total VAr-hours Imported Q2 | acc32 | varh | TotVArh_SF | Total Reactive Power Imported Quadrant 2 |  | O
83 | 84 | 2 | R | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A | acc32 | varh | TotVArh_SF |  |  | O
85 | 86 | 2 | R | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B | acc32 | varh | TotVArh_SF |  |  | O
87 | 88 | 2 | R | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C | acc32 | varh | TotVArh_SF |  |  | O
89 | 90 | 2 | R | TotVArhExpQ3 | Total VAr-hours Exported Q3 | acc32 | varh | TotVArh_SF | Total Reactive Power Exported Quadrant 3 |  | O
91 | 92 | 2 | R | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A | acc32 | varh | TotVArh_SF |  |  | O
93 | 94 | 2 | R | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B | acc32 | varh | TotVArh_SF |  |  | O
95 | 96 | 2 | R | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C | acc32 | varh | TotVArh_SF |  |  | O
97 | 98 | 2 | R | TotVArhExpQ4 | Total VAr-hours Exported Q4 | acc32 | varh | TotVArh_SF | Total Reactive Power Exported Quadrant 4 |  | O
99 | 100 | 2 | R | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A | acc32 | varh | TotVArh_SF |  |  | O
101 | 102 | 2 | R | TotVArhExpQ4PhB | Total VAr-hours Exported Q4 Imported phase B | acc32 | varh | TotVArh_SF |  |  | O
103 | 104 | 2 | R | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C | acc32 | varh | TotVArh_SF |  |  | O
105 | 105 | 1 | R | TotVArh_SF |  | sunssf |  |  | Reactive Energy scale factor |  | O
106 | 107 | 2 | R | Evt | Events | bitfield32 |  |  | Meter Event Flags |  | M
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
M_EVENT_Power_Failure |  |  | 2
M_EVENT_Under_Voltage |  |  | 3
M_EVENT_Low_PF |  |  | 4
M_EVENT_Over_Current |  |  | 5
M_EVENT_Over_Voltage |  |  | 6
M_EVENT_Missing_Sensor |  |  | 7
M_EVENT_Reserved1 |  |  | 8
M_EVENT_Reserved2 |  |  | 9
M_EVENT_Reserved3 |  |  | 10
M_EVENT_Reserved4 |  |  | 11
M_EVENT_Reserved5 |  |  | 12
M_EVENT_Reserved6 |  |  | 13
M_EVENT_Reserved7 |  |  | 14
M_EVENT_Reserved8 |  |  | 15
M_EVENT_OEM01 |  |  | 16
M_EVENT_OEM02 |  |  | 17
M_EVENT_OEM03 |  |  | 18
M_EVENT_OEM04 |  |  | 19
M_EVENT_OEM05 |  |  | 20
M_EVENT_OEM06 |  |  | 21
M_EVENT_OEM07 |  |  | 22
M_EVENT_OEM08 |  |  | 23
M_EVENT_OEM09 |  |  | 24
M_EVENT_OEM10 |  |  | 25
M_EVENT_OEM11 |  |  | 26
M_EVENT_OEM12 |  |  | 27
M_EVENT_OEM13 |  |  | 28
M_EVENT_OEM14 |  |  | 29
M_EVENT_OEM15 |  |  | 30

## M 203
// 203-wye-connect three phase (abcn) meter : ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 203. Uniquely identifies this as a SunSpec wye-connect three phase (abcn) meter Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 105 |  | M
// 203 wye-connect three phase (abcn) meter Fixed Block (105)
3 | 3 | 1 | R | A | Amps | int16 | A | A_SF | Total AC Current |  | M
4 | 4 | 1 | R | AphA | Amps PhaseA | int16 | A | A_SF | Phase A Current |  | M
5 | 5 | 1 | R | AphB | Amps PhaseB | int16 | A | A_SF | Phase B Current |  | M
6 | 6 | 1 | R | AphC | Amps PhaseC | int16 | A | A_SF | Phase C Current |  | M
7 | 7 | 1 | R | A_SF |  | sunssf |  |  | Current scale factor |  | M
8 | 8 | 1 | R | PhV | Voltage LN | int16 | V | V_SF | Line to Neutral AC Voltage (average of active phases) |  | M
9 | 9 | 1 | R | PhVphA | Phase Voltage AN | int16 | V | V_SF | Phase Voltage AN |  | M
10 | 10 | 1 | R | PhVphB | Phase Voltage BN | int16 | V | V_SF | Phase Voltage BN |  | M
11 | 11 | 1 | R | PhVphC | Phase Voltage CN | int16 | V | V_SF | Phase Voltage CN |  | M
12 | 12 | 1 | R | PPV | Voltage LL | int16 | V | V_SF | Line to Line AC Voltage (average of active phases) |  | M
13 | 13 | 1 | R | PhVphAB |  | int16 | V | V_SF |  |  | M
14 | 14 | 1 | R | PhVphBC |  | int16 | V | V_SF |  |  | M
15 | 15 | 1 | R | PhVphCA |  | int16 | V | V_SF |  |  | M
16 | 16 | 1 | R | V_SF |  | sunssf |  |  | Voltage scale factor |  | M
17 | 17 | 1 | R | Hz | Hz | int16 | Hz | Hz_SF | Frequency |  | M
18 | 18 | 1 | R | Hz_SF |  | sunssf |  |  | Frequency scale factor |  | O
19 | 19 | 1 | R | W | Watts | int16 | W | W_SF | Total Real Power |  | M
20 | 20 | 1 | R | WphA | Watts phase A | int16 | W | W_SF |  |  | O
21 | 21 | 1 | R | WphB | Watts phase B | int16 | W | W_SF |  |  | O
22 | 22 | 1 | R | WphC | Watts phase C | int16 | W | W_SF |  |  | O
23 | 23 | 1 | R | W_SF |  | sunssf |  |  | Real Power scale factor |  | M
24 | 24 | 1 | R | VA | VA | int16 | VA | VA_SF | AC Apparent Power |  | O
25 | 25 | 1 | R | VAphA | VA phase A | int16 | VA | VA_SF |  |  | O
26 | 26 | 1 | R | VAphB | VA phase B | int16 | VA | VA_SF |  |  | O
27 | 27 | 1 | R | VAphC | VA phase C | int16 | VA | VA_SF |  |  | O
28 | 28 | 1 | R | VA_SF |  | sunssf |  |  | Apparent Power scale factor |  | O
29 | 29 | 1 | R | VAR | VAR | int16 | var | VAR_SF | Reactive Power |  | O
30 | 30 | 1 | R | VARphA | VAR phase A | int16 | var | VAR_SF |  |  | O
31 | 31 | 1 | R | VARphB | VAR phase B | int16 | var | VAR_SF |  |  | O
32 | 32 | 1 | R | VARphC | VAR phase C | int16 | var | VAR_SF |  |  | O
33 | 33 | 1 | R | VAR_SF |  | sunssf |  |  | Reactive Power scale factor |  | O
34 | 34 | 1 | R | PF | PF | int16 | Pct | PF_SF | Power Factor |  | O
35 | 35 | 1 | R | PFphA | PF phase A | int16 | Pct | PF_SF |  |  | O
36 | 36 | 1 | R | PFphB | PF phase B | int16 | Pct | PF_SF |  |  | O
37 | 37 | 1 | R | PFphC | PF phase C | int16 | Pct | PF_SF |  |  | O
38 | 38 | 1 | R | PF_SF |  | sunssf |  |  | Power Factor scale factor |  | O
39 | 40 | 2 | R | TotWhExp | Total Watt-hours Exported | acc32 | Wh | TotWh_SF | Total Real Energy Exported |  | M
41 | 42 | 2 | R | TotWhExpPhA | Total Watt-hours Exported phase A | acc32 | Wh | TotWh_SF |  |  | O
43 | 44 | 2 | R | TotWhExpPhB | Total Watt-hours Exported phase B | acc32 | Wh | TotWh_SF |  |  | O
45 | 46 | 2 | R | TotWhExpPhC | Total Watt-hours Exported phase C | acc32 | Wh | TotWh_SF |  |  | O
47 | 48 | 2 | R | TotWhImp | Total Watt-hours Imported | acc32 | Wh | TotWh_SF | Total Real Energy Imported |  | M
49 | 50 | 2 | R | TotWhImpPhA | Total Watt-hours Imported phase A | acc32 | Wh | TotWh_SF |  |  | O
51 | 52 | 2 | R | TotWhImpPhB | Total Watt-hours Imported phase B | acc32 | Wh | TotWh_SF |  |  | O
53 | 54 | 2 | R | TotWhImpPhC | Total Watt-hours Imported phase C | acc32 | Wh | TotWh_SF |  |  | O
55 | 55 | 1 | R | TotWh_SF |  | sunssf |  |  | Real Energy scale factor |  | M
56 | 57 | 2 | R | TotVAhExp | Total VA-hours Exported | acc32 | VAh | TotVAh_SF | Total Apparent Energy Exported |  | O
58 | 59 | 2 | R | TotVAhExpPhA | Total VA-hours Exported phase A | acc32 | VAh | TotVAh_SF |  |  | O
60 | 61 | 2 | R | TotVAhExpPhB | Total VA-hours Exported phase B | acc32 | VAh | TotVAh_SF |  |  | O
62 | 63 | 2 | R | TotVAhExpPhC | Total VA-hours Exported phase C | acc32 | VAh | TotVAh_SF |  |  | O
64 | 65 | 2 | R | TotVAhImp | Total VA-hours Imported | acc32 | VAh | TotVAh_SF | Total Apparent Energy Imported |  | O
66 | 67 | 2 | R | TotVAhImpPhA | Total VA-hours Imported phase A | acc32 | VAh | TotVAh_SF |  |  | O
68 | 69 | 2 | R | TotVAhImpPhB | Total VA-hours Imported phase B | acc32 | VAh | TotVAh_SF |  |  | O
70 | 71 | 2 | R | TotVAhImpPhC | Total VA-hours Imported phase C | acc32 | VAh | TotVAh_SF |  |  | O
72 | 72 | 1 | R | TotVAh_SF |  | sunssf |  |  | Apparent Energy scale factor |  | O
73 | 74 | 2 | R | TotVArhImpQ1 | Total VAR-hours Imported Q1 | acc32 | varh | TotVArh_SF | Total Reactive Energy Imported Quadrant 1 |  | O
75 | 76 | 2 | R | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A | acc32 | varh | TotVArh_SF |  |  | O
77 | 78 | 2 | R | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B | acc32 | varh | TotVArh_SF |  |  | O
79 | 80 | 2 | R | TotVArhImpQ1PhC | Total VAr-hourse Imported Q1 phase C | acc32 | varh | TotVArh_SF |  |  | O
81 | 82 | 2 | R | TotVArhImpQ2 | Total VAr-hours Imported Q2 | acc32 | varh | TotVArh_SF | Total Reactive Power Imported Quadrant 2 |  | O
83 | 84 | 2 | R | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A | acc32 | varh | TotVArh_SF |  |  | O
85 | 86 | 2 | R | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B | acc32 | varh | TotVArh_SF |  |  | O
87 | 88 | 2 | R | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C | acc32 | varh | TotVArh_SF |  |  | O
89 | 90 | 2 | R | TotVArhExpQ3 | Total VAr-hours Exported Q3 | acc32 | varh | TotVArh_SF | Total Reactive Power Exported Quadrant 3 |  | O
91 | 92 | 2 | R | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A | acc32 | varh | TotVArh_SF |  |  | O
93 | 94 | 2 | R | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B | acc32 | varh | TotVArh_SF |  |  | O
95 | 96 | 2 | R | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C | acc32 | varh | TotVArh_SF |  |  | O
97 | 98 | 2 | R | TotVArhExpQ4 | Total VAr-hours Exported Q4 | acc32 | varh | TotVArh_SF | Total Reactive Power Exported Quadrant 4 |  | O
99 | 100 | 2 | R | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A | acc32 | varh | TotVArh_SF |  |  | O
101 | 102 | 2 | R | TotVArhExpQ4PhB |  | acc32 | varh | TotVArh_SF |  |  | O
103 | 104 | 2 | R | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C | acc32 | varh | TotVArh_SF |  |  | O
105 | 105 | 1 | R | TotVArh_SF |  | sunssf |  |  | Reactive Energy scale factor |  | O
106 | 107 | 2 | R | Evt | Events | bitfield32 |  |  | Meter Event Flags |  | M
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
M_EVENT_Power_Failure |  |  | 2
M_EVENT_Under_Voltage |  |  | 3
M_EVENT_Low_PF |  |  | 4
M_EVENT_Over_Current |  |  | 5
M_EVENT_Over_Voltage |  |  | 6
M_EVENT_Missing_Sensor |  |  | 7
M_EVENT_Reserved1 |  |  | 8
M_EVENT_Reserved2 |  |  | 9
M_EVENT_Reserved3 |  |  | 10
M_EVENT_Reserved4 |  |  | 11
M_EVENT_Reserved5 |  |  | 12
M_EVENT_Reserved6 |  |  | 13
M_EVENT_Reserved7 |  |  | 14
M_EVENT_Reserved8 |  |  | 15
M_EVENT_OEM01 |  |  | 16
M_EVENT_OEM02 |  |  | 17
M_EVENT_OEM03 |  |  | 18
M_EVENT_OEM04 |  |  | 19
M_EVENT_OEM05 |  |  | 20
M_EVENT_OEM06 |  |  | 21
M_EVENT_OEM07 |  |  | 22
M_EVENT_OEM08 |  |  | 23
M_EVENT_OEM09 |  |  | 24
M_EVENT_OEM10 |  |  | 25
M_EVENT_OEM11 |  |  | 26
M_EVENT_OEM12 |  |  | 27
M_EVENT_OEM13 |  |  | 28
M_EVENT_OEM14 |  |  | 29
M_EVENT_OEM15 |  |  | 30

## M 204
// 204-delta-connect three phase (abc) meter : ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 204. Uniquely identifies this as a SunSpec delta-connect three phase (abc) meter Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 105 |  | M
// 204 delta-connect three phase (abc) meter Fixed Block (105)
3 | 3 | 1 | R | A | Amps | int16 | A | A_SF | Total AC Current |  | M
4 | 4 | 1 | R | AphA | Amps PhaseA | int16 | A | A_SF | Phase A Current |  | M
5 | 5 | 1 | R | AphB | Amps PhaseB | int16 | A | A_SF | Phase B Current |  | M
6 | 6 | 1 | R | AphC | Amps PhaseC | int16 | A | A_SF | Phase C Current |  | M
7 | 7 | 1 | R | A_SF |  | sunssf |  |  | Current scale factor |  | M
8 | 8 | 1 | R | PhV | Voltage LN | int16 | V | V_SF | Line to Neutral AC Voltage (average of active phases) |  | O
9 | 9 | 1 | R | PhVphA | Phase Voltage AN | int16 | V | V_SF | Phase Voltage AN |  | O
10 | 10 | 1 | R | PhVphB | Phase Voltage BN | int16 | V | V_SF | Phase Voltage BN |  | O
11 | 11 | 1 | R | PhVphC | Phase Voltage CN | int16 | V | V_SF | Phase Voltage CN |  | O
12 | 12 | 1 | R | PPV | Voltage LL | int16 | V | V_SF | Line to Line AC Voltage (average of active phases) |  | M
13 | 13 | 1 | R | PhVphAB |  | int16 | V | V_SF |  |  | M
14 | 14 | 1 | R | PhVphBC |  | int16 | V | V_SF |  |  | M
15 | 15 | 1 | R | PhVphCA |  | int16 | V | V_SF |  |  | M
16 | 16 | 1 | R | V_SF |  | sunssf |  |  | Voltage scale factor |  | M
17 | 17 | 1 | R | Hz | Hz | int16 | Hz | Hz_SF | Frequency |  | M
18 | 18 | 1 | R | Hz_SF |  | sunssf |  |  | Frequency scale factor |  | O
19 | 19 | 1 | R | W | Watts | int16 | W | W_SF | Total Real Power |  | M
20 | 20 | 1 | R | WphA | Watts phase A | int16 | W | W_SF |  |  | O
21 | 21 | 1 | R | WphB | Watts phase B | int16 | W | W_SF |  |  | O
22 | 22 | 1 | R | WphC | Watts phase C | int16 | W | W_SF |  |  | O
23 | 23 | 1 | R | W_SF |  | sunssf |  |  | Real Power scale factor |  | M
24 | 24 | 1 | R | VA | VA | int16 | VA | VA_SF | AC Apparent Power |  | O
25 | 25 | 1 | R | VAphA | VA phase A | int16 | VA | VA_SF |  |  | O
26 | 26 | 1 | R | VAphB | VA phase B | int16 | VA | VA_SF |  |  | O
27 | 27 | 1 | R | VAphC | VA phase C | int16 | VA | VA_SF |  |  | O
28 | 28 | 1 | R | VA_SF |  | sunssf |  |  | Apparent Power scale factor |  | O
29 | 29 | 1 | R | VAR | VAR | int16 | var | VAR_SF | Reactive Power |  | O
30 | 30 | 1 | R | VARphA | VAR phase A | int16 | var | VAR_SF |  |  | O
31 | 31 | 1 | R | VARphB | VAR phase B | int16 | var | VAR_SF |  |  | O
32 | 32 | 1 | R | VARphC | VAR phase C | int16 | var | VAR_SF |  |  | O
33 | 33 | 1 | R | VAR_SF |  | sunssf |  |  | Reactive Power scale factor |  | O
34 | 34 | 1 | R | PF | PF | int16 | Pct | PF_SF | Power Factor |  | O
35 | 35 | 1 | R | PFphA | PF phase A | int16 | Pct | PF_SF |  |  | O
36 | 36 | 1 | R | PFphB | PF phase B | int16 | Pct | PF_SF |  |  | O
37 | 37 | 1 | R | PFphC | PF phase C | int16 | Pct | PF_SF |  |  | O
38 | 38 | 1 | R | PF_SF |  | sunssf |  |  | Power Factor scale factor |  | O
39 | 40 | 2 | R | TotWhExp | Total Watt-hours Exported | acc32 | Wh | TotWh_SF | Total Real Energy Exported |  | M
41 | 42 | 2 | R | TotWhExpPhA | Total Watt-hours Exported phase A | acc32 | Wh | TotWh_SF |  |  | O
43 | 44 | 2 | R | TotWhExpPhB | Total Watt-hours Exported phase B | acc32 | Wh | TotWh_SF |  |  | O
45 | 46 | 2 | R | TotWhExpPhC | Total Watt-hours Exported phase C | acc32 | Wh | TotWh_SF |  |  | O
47 | 48 | 2 | R | TotWhImp | Total Watt-hours Imported | acc32 | Wh | TotWh_SF | Total Real Energy Imported |  | M
49 | 50 | 2 | R | TotWhImpPhA | Total Watt-hours Imported phase A | acc32 | Wh | TotWh_SF |  |  | O
51 | 52 | 2 | R | TotWhImpPhB | Total Watt-hours Imported phase B | acc32 | Wh | TotWh_SF |  |  | O
53 | 54 | 2 | R | TotWhImpPhC | Total Watt-hours Imported phase C | acc32 | Wh | TotWh_SF |  |  | O
55 | 55 | 1 | R | TotWh_SF |  | sunssf |  |  | Real Energy scale factor |  | M
56 | 57 | 2 | R | TotVAhExp | Total VA-hours Exported | acc32 | VAh | TotVAh_SF | Total Apparent Energy Exported |  | O
58 | 59 | 2 | R | TotVAhExpPhA | Total VA-hours Exported phase A | acc32 | VAh | TotVAh_SF |  |  | O
60 | 61 | 2 | R | TotVAhExpPhB | Total VA-hours Exported phase B | acc32 | VAh | TotVAh_SF |  |  | O
62 | 63 | 2 | R | TotVAhExpPhC | Total VA-hours Exported phase C | acc32 | VAh | TotVAh_SF |  |  | O
64 | 65 | 2 | R | TotVAhImp | Total VA-hours Imported | acc32 | VAh | TotVAh_SF | Total Apparent Energy Imported |  | O
66 | 67 | 2 | R | TotVAhImpPhA | Total VA-hours Imported phase A | acc32 | VAh | TotVAh_SF |  |  | O
68 | 69 | 2 | R | TotVAhImpPhB | Total VA-hours Imported phase B | acc32 | VAh | TotVAh_SF |  |  | O
70 | 71 | 2 | R | TotVAhImpPhC | Total VA-hours Imported phase C | acc32 | VAh | TotVAh_SF |  |  | O
72 | 72 | 1 | R | TotVAh_SF |  | sunssf |  |  | Apparent Energy scale factor |  | O
73 | 74 | 2 | R | TotVArhImpQ1 | Total VAR-hours Imported Q1 | acc32 | varh | TotVArh_SF | Total Reactive Energy Imported Quadrant 1 |  | O
75 | 76 | 2 | R | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A | acc32 | varh | TotVArh_SF |  |  | O
77 | 78 | 2 | R | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B | acc32 | varh | TotVArh_SF |  |  | O
79 | 80 | 2 | R | TotVArhImpQ1PhC | Total VAr-hourse Imported Q1 phase C | acc32 | varh | TotVArh_SF |  |  | O
81 | 82 | 2 | R | TotVArhImpQ2 | Total VAr-hours Imported Q2 | acc32 | varh | TotVArh_SF | Total Reactive Power Imported Quadrant 2 |  | O
83 | 84 | 2 | R | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A | acc32 | varh | TotVArh_SF |  |  | O
85 | 86 | 2 | R | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B | acc32 | varh | TotVArh_SF |  |  | O
87 | 88 | 2 | R | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C | acc32 | varh | TotVArh_SF |  |  | O
89 | 90 | 2 | R | TotVArhExpQ3 | Total VAr-hours Exported Q3 | acc32 | varh | TotVArh_SF | Total Reactive Power Exported Quadrant 3 |  | O
91 | 92 | 2 | R | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A | acc32 | varh | TotVArh_SF |  |  | O
93 | 94 | 2 | R | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B | acc32 | varh | TotVArh_SF |  |  | O
95 | 96 | 2 | R | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C | acc32 | varh | TotVArh_SF |  |  | O
97 | 98 | 2 | R | TotVArhExpQ4 | Total VAr-hours Exported Q4 | acc32 | varh | TotVArh_SF | Total Reactive Power Exported Quadrant 4 |  | O
99 | 100 | 2 | R | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A | acc32 | varh | TotVArh_SF |  |  | O
101 | 102 | 2 | R | TotVArhExpQ4PhB |  | acc32 | varh | TotVArh_SF |  |  | O
103 | 104 | 2 | R | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C | acc32 | varh | TotVArh_SF |  |  | O
105 | 105 | 1 | R | TotVArh_SF |  | sunssf |  |  | Reactive Energy scale factor |  | O
106 | 107 | 2 | R | Evt | Events | bitfield32 |  |  | Meter Event Flags |  | M
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
M_EVENT_Power_Failure |  |  | 2
M_EVENT_Under_Voltage |  |  | 3
M_EVENT_Low_PF |  |  | 4
M_EVENT_Over_Current |  |  | 5
M_EVENT_Over_Voltage |  |  | 6
M_EVENT_Missing_Sensor |  |  | 7
M_EVENT_Reserved1 |  |  | 8
M_EVENT_Reserved2 |  |  | 9
M_EVENT_Reserved3 |  |  | 10
M_EVENT_Reserved4 |  |  | 11
M_EVENT_Reserved5 |  |  | 12
M_EVENT_Reserved6 |  |  | 13
M_EVENT_Reserved7 |  |  | 14
M_EVENT_Reserved8 |  |  | 15
M_EVENT_OEM01 |  |  | 16
M_EVENT_OEM02 |  |  | 17
M_EVENT_OEM03 |  |  | 18
M_EVENT_OEM04 |  |  | 19
M_EVENT_OEM05 |  |  | 20
M_EVENT_OEM06 |  |  | 21
M_EVENT_OEM07 |  |  | 22
M_EVENT_OEM08 |  |  | 23
M_EVENT_OEM09 |  |  | 24
M_EVENT_OEM10 |  |  | 25
M_EVENT_OEM11 |  |  | 26
M_EVENT_OEM12 |  |  | 27
M_EVENT_OEM13 |  |  | 28
M_EVENT_OEM14 |  |  | 29
M_EVENT_OEM15 |  |  | 30

## M 211
// 211-single phase (AN or AB) meter : (Float)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 211. Uniquely identifies this as a SunSpec single phase (AN or AB) meter Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 124 |  | M
// 211 single phase (AN or AB) meter Fixed Block (124)
3 | 4 | 2 | R | A | Amps | float32 | A |  | Total AC Current |  | M
5 | 6 | 2 | R | AphA | Amps PhaseA | float32 | A |  | Phase A Current |  | M
7 | 8 | 2 | R | AphB | Amps PhaseB | float32 | A |  | Phase B Current |  | O
9 | 10 | 2 | R | AphC | Amps PhaseC | float32 | A |  | Phase C Current |  | O
11 | 12 | 2 | R | PhV | Voltage LN | float32 | V |  | Line to Neutral AC Voltage (average of active phases) |  | O
13 | 14 | 2 | R | PhVphA | Phase Voltage AN | float32 | V |  | Phase Voltage AN |  | O
15 | 16 | 2 | R | PhVphB | Phase Voltage BN | float32 | V |  | Phase Voltage BN |  | O
17 | 18 | 2 | R | PhVphC | Phase Voltage CN | float32 | V |  | Phase Voltage CN |  | O
19 | 20 | 2 | R | PPV | Voltage LL | float32 | V |  | Line to Line AC Voltage (average of active phases) |  | O
21 | 22 | 2 | R | PPVphAB | Phase Voltage AB | float32 | V |  | Phase Voltage AB |  | O
23 | 24 | 2 | R | PPVphBC | Phase Voltage BC | float32 | V |  | Phase Voltage BC |  | O
25 | 26 | 2 | R | PPVphCA | Phase Voltage CA | float32 | V |  | Phase Voltage CA |  | O
27 | 28 | 2 | R | Hz | Hz | float32 | Hz |  | Frequency |  | M
29 | 30 | 2 | R | W | Watts | float32 | W |  | Total Real Power |  | M
31 | 32 | 2 | R | WphA | Watts phase A | float32 | W |  |  |  | O
33 | 34 | 2 | R | WphB | Watts phase B | float32 | W |  |  |  | O
35 | 36 | 2 | R | WphC | Watts phase C | float32 | W |  |  |  | O
37 | 38 | 2 | R | VA | VA | float32 | VA |  | AC Apparent Power |  | O
39 | 40 | 2 | R | VAphA | VA phase A | float32 | VA |  |  |  | O
41 | 42 | 2 | R | VAphB | VA phase B | float32 | VA |  |  |  | O
43 | 44 | 2 | R | VAphC | VA phase C | float32 | VA |  |  |  | O
45 | 46 | 2 | R | VAR | VAR | float32 | var |  | Reactive Power |  | O
47 | 48 | 2 | R | VARphA | VAR phase A | float32 | var |  |  |  | O
49 | 50 | 2 | R | VARphB | VAR phase B | float32 | var |  |  |  | O
51 | 52 | 2 | R | VARphC | VAR phase C | float32 | var |  |  |  | O
53 | 54 | 2 | R | PF | PF | float32 | PF |  | Power Factor |  | O
55 | 56 | 2 | R | PFphA | PF phase A | float32 | PF |  |  |  | O
57 | 58 | 2 | R | PFphB | PF phase B | float32 | PF |  |  |  | O
59 | 60 | 2 | R | PFphC | PF phase C | float32 | PF |  |  |  | O
61 | 62 | 2 | R | TotWhExp | Total Watt-hours Exported | acc32 | Wh |  | Total Real Energy Exported |  | M
63 | 64 | 2 | R | TotWhExpPhA | Total Watt-hours Exported phase A | acc32 | Wh |  |  |  | O
65 | 66 | 2 | R | TotWhExpPhB | Total Watt-hours Exported phase B | acc32 | Wh |  |  |  | O
67 | 68 | 2 | R | TotWhExpPhC | Total Watt-hours Exported phase C | acc32 | Wh |  |  |  | O
69 | 70 | 2 | R | TotWhImp | Total Watt-hours Imported | acc32 | Wh |  | Total Real Energy Imported |  | M
71 | 72 | 2 | R | TotWhImpPhA | Total Watt-hours Imported phase A | acc32 | Wh |  |  |  | O
73 | 74 | 2 | R | TotWhImpPhB | Total Watt-hours Imported phase B | acc32 | Wh |  |  |  | O
75 | 76 | 2 | R | TotWhImpPhC | Total Watt-hours Imported phase C | acc32 | Wh |  |  |  | O
77 | 78 | 2 | R | TotVAhExp | Total VA-hours Exported | acc32 | VAh |  | Total Apparent Energy Exported |  | O
79 | 80 | 2 | R | TotVAhExpPhA | Total VA-hours Exported phase A | acc32 | VAh |  |  |  | O
81 | 82 | 2 | R | TotVAhExpPhB | Total VA-hours Exported phase B | acc32 | VAh |  |  |  | O
83 | 84 | 2 | R | TotVAhExpPhC | Total VA-hours Exported phase C | acc32 | VAh |  |  |  | O
85 | 86 | 2 | R | TotVAhImp | Total VA-hours Imported | acc32 | VAh |  | Total Apparent Energy Imported |  | O
87 | 88 | 2 | R | TotVAhImpPhA | Total VA-hours Imported phase A | acc32 | VAh |  |  |  | O
89 | 90 | 2 | R | TotVAhImpPhB | Total VA-hours Imported phase B | acc32 | VAh |  |  |  | O
91 | 92 | 2 | R | TotVAhImpPhC | Total VA-hours Imported phase C | acc32 | VAh |  |  |  | O
93 | 94 | 2 | R | TotVArhImpQ1 | Total VAR-hours Imported Q1 | acc32 | varh |  | Total Reactive Energy Imported Quadrant 1 |  | O
95 | 96 | 2 | R | TotVArhImpQ1phA |  | acc32 | varh |  |  |  | O
97 | 98 | 2 | R | TotVArhImpQ1phB |  | acc32 | varh |  |  |  | O
99 | 100 | 2 | R | TotVArhImpQ1phC |  | acc32 | varh |  |  |  | O
101 | 102 | 2 | R | TotVArhImpQ2 | Total VAr-hours Imported Q2 | acc32 | varh |  | Total Reactive Power Imported Quadrant 2 |  | O
103 | 104 | 2 | R | TotVArhImpQ2phA |  | acc32 | varh |  |  |  | O
105 | 106 | 2 | R | TotVArhImpQ2phB |  | acc32 | varh |  |  |  | O
107 | 108 | 2 | R | TotVArhImpQ2phC |  | acc32 | varh |  |  |  | O
109 | 110 | 2 | R | TotVArhExpQ3 | Total VAr-hours Exported Q3 | acc32 | varh |  | Total Reactive Power Exported Quadrant 3 |  | O
111 | 112 | 2 | R | TotVArhExpQ3phA |  | acc32 | varh |  |  |  | O
113 | 114 | 2 | R | TotVArhExpQ3phB |  | acc32 | varh |  |  |  | O
115 | 116 | 2 | R | TotVArhExpQ3phC |  | acc32 | varh |  |  |  | O
117 | 118 | 2 | R | TotVArhExpQ4 | Total VAr-hours Exported Q4 | acc32 | varh |  | Total Reactive Power Exported Quadrant 4 |  | O
119 | 120 | 2 | R | TotVArhExpQ4phA |  | acc32 | varh |  |  |  | O
121 | 122 | 2 | R | TotVArhExpQ4phB |  | acc32 | varh |  |  |  | O
123 | 124 | 2 | R | TotVArhExpQ4phC |  | acc32 | varh |  |  |  | O
125 | 126 | 2 | R | Evt | Events | bitfield32 |  |  | Meter Event Flags |  | M
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
M_EVENT_Power_Failure |  |  | 2
M_EVENT_Under_Voltage |  |  | 3
M_EVENT_Low_PF |  |  | 4
M_EVENT_Over_Current |  |  | 5
M_EVENT_Over_Voltage |  |  | 6
M_EVENT_Missing_Sensor |  |  | 7
M_EVENT_Reserved1 |  |  | 8
M_EVENT_Reserved2 |  |  | 9
M_EVENT_Reserved3 |  |  | 10
M_EVENT_Reserved4 |  |  | 11
M_EVENT_Reserved5 |  |  | 12
M_EVENT_Reserved6 |  |  | 13
M_EVENT_Reserved7 |  |  | 14
M_EVENT_Reserved8 |  |  | 15
M_EVENT_OEM01 |  |  | 16
M_EVENT_OEM02 |  |  | 17
M_EVENT_OEM03 |  |  | 18
M_EVENT_OEM04 |  |  | 19
M_EVENT_OEM05 |  |  | 20
M_EVENT_OEM06 |  |  | 21
M_EVENT_OEM07 |  |  | 22
M_EVENT_OEM08 |  |  | 23
M_EVENT_OEM09 |  |  | 24
M_EVENT_OEM10 |  |  | 25
M_EVENT_OEM11 |  |  | 26
M_EVENT_OEM12 |  |  | 27
M_EVENT_OEM13 |  |  | 28
M_EVENT_OEM14 |  |  | 29
M_EVENT_OEM15 |  |  | 30

## M 212
// 212-split single phase (ABN) meter : (Float)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 212. Uniquely identifies this as a SunSpec split single phase (ABN) meter Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 124 |  | M
// 212 split single phase (ABN) meter Fixed Block (124)
3 | 4 | 2 | R | A | Amps | float32 | A |  | Total AC Current |  | M
5 | 6 | 2 | R | AphA | Amps PhaseA | float32 | A |  | Phase A Current |  | M
7 | 8 | 2 | R | AphB | Amps PhaseB | float32 | A |  | Phase B Current |  | M
9 | 10 | 2 | R | AphC | Amps PhaseC | float32 | A |  | Phase C Current |  | O
11 | 12 | 2 | R | PhV | Voltage LN | float32 | V |  | Line to Neutral AC Voltage (average of active phases) |  | M
13 | 14 | 2 | R | PhVphA | Phase Voltage AN | float32 | V |  | Phase Voltage AN |  | M
15 | 16 | 2 | R | PhVphB | Phase Voltage BN | float32 | V |  | Phase Voltage BN |  | M
17 | 18 | 2 | R | PhVphC | Phase Voltage CN | float32 | V |  | Phase Voltage CN |  | O
19 | 20 | 2 | R | PPV | Voltage LL | float32 | V |  | Line to Line AC Voltage (average of active phases) |  | M
21 | 22 | 2 | R | PPVphAB | Phase Voltage AB | float32 | V |  | Phase Voltage AB |  | M
23 | 24 | 2 | R | PPVphBC | Phase Voltage BC | float32 | V |  | Phase Voltage BC |  | O
25 | 26 | 2 | R | PPVphCA | Phase Voltage CA | float32 | V |  | Phase Voltage CA |  | O
27 | 28 | 2 | R | Hz | Hz | float32 | Hz |  | Frequency |  | M
29 | 30 | 2 | R | W | Watts | float32 | W |  | Total Real Power |  | M
31 | 32 | 2 | R | WphA | Watts phase A | float32 | W |  |  |  | O
33 | 34 | 2 | R | WphB | Watts phase B | float32 | W |  |  |  | O
35 | 36 | 2 | R | WphC | Watts phase C | float32 | W |  |  |  | O
37 | 38 | 2 | R | VA | VA | float32 | VA |  | AC Apparent Power |  | O
39 | 40 | 2 | R | VAphA | VA phase A | float32 | VA |  |  |  | O
41 | 42 | 2 | R | VAphB | VA phase B | float32 | VA |  |  |  | O
43 | 44 | 2 | R | VAphC | VA phase C | float32 | VA |  |  |  | O
45 | 46 | 2 | R | VAR | VAR | float32 | var |  | Reactive Power |  | O
47 | 48 | 2 | R | VARphA | VAR phase A | float32 | var |  |  |  | O
49 | 50 | 2 | R | VARphB | VAR phase B | float32 | var |  |  |  | O
51 | 52 | 2 | R | VARphC | VAR phase C | float32 | var |  |  |  | O
53 | 54 | 2 | R | PF | PF | float32 | PF |  | Power Factor |  | O
55 | 56 | 2 | R | PFphA | PF phase A | float32 | PF |  |  |  | O
57 | 58 | 2 | R | PFphB | PF phase B | float32 | PF |  |  |  | O
59 | 60 | 2 | R | PFphC | PF phase C | float32 | PF |  |  |  | O
61 | 62 | 2 | R | TotWhExp | Total Watt-hours Exported | acc32 | Wh |  | Total Real Energy Exported |  | M
63 | 64 | 2 | R | TotWhExpPhA | Total Watt-hours Exported phase A | acc32 | Wh |  |  |  | O
65 | 66 | 2 | R | TotWhExpPhB | Total Watt-hours Exported phase B | acc32 | Wh |  |  |  | O
67 | 68 | 2 | R | TotWhExpPhC | Total Watt-hours Exported phase C | acc32 | Wh |  |  |  | O
69 | 70 | 2 | R | TotWhImp | Total Watt-hours Imported | acc32 | Wh |  | Total Real Energy Imported |  | M
71 | 72 | 2 | R | TotWhImpPhA | Total Watt-hours Imported phase A | acc32 | Wh |  |  |  | O
73 | 74 | 2 | R | TotWhImpPhB | Total Watt-hours Imported phase B | acc32 | Wh |  |  |  | O
75 | 76 | 2 | R | TotWhImpPhC | Total Watt-hours Imported phase C | acc32 | Wh |  |  |  | O
77 | 78 | 2 | R | TotVAhExp | Total VA-hours Exported | acc32 | VAh |  | Total Apparent Energy Exported |  | O
79 | 80 | 2 | R | TotVAhExpPhA | Total VA-hours Exported phase A | acc32 | VAh |  |  |  | O
81 | 82 | 2 | R | TotVAhExpPhB | Total VA-hours Exported phase B | acc32 | VAh |  |  |  | O
83 | 84 | 2 | R | TotVAhExpPhC | Total VA-hours Exported phase C | acc32 | VAh |  |  |  | O
85 | 86 | 2 | R | TotVAhImp | Total VA-hours Imported | acc32 | VAh |  | Total Apparent Energy Imported |  | O
87 | 88 | 2 | R | TotVAhImpPhA | Total VA-hours Imported phase A | acc32 | VAh |  |  |  | O
89 | 90 | 2 | R | TotVAhImpPhB | Total VA-hours Imported phase B | acc32 | VAh |  |  |  | O
91 | 92 | 2 | R | TotVAhImpPhC | Total VA-hours Imported phase C | acc32 | VAh |  |  |  | O
93 | 94 | 2 | R | TotVArhImpQ1 | Total VAR-hours Imported Q1 | acc32 | varh |  | Total Reactive Energy Imported Quadrant 1 |  | O
95 | 96 | 2 | R | TotVArhImpQ1phA |  | acc32 | varh |  |  |  | O
97 | 98 | 2 | R | TotVArhImpQ1phB |  | acc32 | varh |  |  |  | O
99 | 100 | 2 | R | TotVArhImpQ1phC |  | acc32 | varh |  |  |  | O
101 | 102 | 2 | R | TotVArhImpQ2 | Total VAr-hours Imported Q2 | acc32 | varh |  | Total Reactive Power Imported Quadrant 2 |  | O
103 | 104 | 2 | R | TotVArhImpQ2phA |  | acc32 | varh |  |  |  | O
105 | 106 | 2 | R | TotVArhImpQ2phB |  | acc32 | varh |  |  |  | O
107 | 108 | 2 | R | TotVArhImpQ2phC |  | acc32 | varh |  |  |  | O
109 | 110 | 2 | R | TotVArhExpQ3 | Total VAr-hours Exported Q3 | acc32 | varh |  | Total Reactive Power Exported Quadrant 3 |  | O
111 | 112 | 2 | R | TotVArhExpQ3phA |  | acc32 | varh |  |  |  | O
113 | 114 | 2 | R | TotVArhExpQ3phB |  | acc32 | varh |  |  |  | O
115 | 116 | 2 | R | TotVArhExpQ3phC |  | acc32 | varh |  |  |  | O
117 | 118 | 2 | R | TotVArhExpQ4 | Total VAr-hours Exported Q4 | acc32 | varh |  | Total Reactive Power Exported Quadrant 4 |  | O
119 | 120 | 2 | R | TotVArhExpQ4phA |  | acc32 | varh |  |  |  | O
121 | 122 | 2 | R | TotVArhExpQ4phB |  | acc32 | varh |  |  |  | O
123 | 124 | 2 | R | TotVArhExpQ4phC |  | acc32 | varh |  |  |  | O
125 | 126 | 2 | R | Evt | Events | bitfield32 |  |  | Meter Event Flags |  | M
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
M_EVENT_Power_Failure |  |  | 2
M_EVENT_Under_Voltage |  |  | 3
M_EVENT_Low_PF |  |  | 4
M_EVENT_Over_Current |  |  | 5
M_EVENT_Over_Voltage |  |  | 6
M_EVENT_Missing_Sensor |  |  | 7
M_EVENT_Reserved1 |  |  | 8
M_EVENT_Reserved2 |  |  | 9
M_EVENT_Reserved3 |  |  | 10
M_EVENT_Reserved4 |  |  | 11
M_EVENT_Reserved5 |  |  | 12
M_EVENT_Reserved6 |  |  | 13
M_EVENT_Reserved7 |  |  | 14
M_EVENT_Reserved8 |  |  | 15
M_EVENT_OEM01 |  |  | 16
M_EVENT_OEM02 |  |  | 17
M_EVENT_OEM03 |  |  | 18
M_EVENT_OEM04 |  |  | 19
M_EVENT_OEM05 |  |  | 20
M_EVENT_OEM06 |  |  | 21
M_EVENT_OEM07 |  |  | 22
M_EVENT_OEM08 |  |  | 23
M_EVENT_OEM09 |  |  | 24
M_EVENT_OEM10 |  |  | 25
M_EVENT_OEM11 |  |  | 26
M_EVENT_OEM12 |  |  | 27
M_EVENT_OEM13 |  |  | 28
M_EVENT_OEM14 |  |  | 29
M_EVENT_OEM15 |  |  | 30

## M 213
// 213-wye-connect three phase (abcn) meter : (Float)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 213. Uniquely identifies this as a SunSpec wye-connect three phase (abcn) meter Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 124 |  | M
// 213 wye-connect three phase (abcn) meter Fixed Block (124)
3 | 4 | 2 | R | A | Amps | float32 | A |  | Total AC Current |  | M
5 | 6 | 2 | R | AphA | Amps PhaseA | float32 | A |  | Phase A Current |  | M
7 | 8 | 2 | R | AphB | Amps PhaseB | float32 | A |  | Phase B Current |  | M
9 | 10 | 2 | R | AphC | Amps PhaseC | float32 | A |  | Phase C Current |  | M
11 | 12 | 2 | R | PhV | Voltage LN | float32 | V |  | Line to Neutral AC Voltage (average of active phases) |  | M
13 | 14 | 2 | R | PhVphA | Phase Voltage AN | float32 | V |  | Phase Voltage AN |  | M
15 | 16 | 2 | R | PhVphB | Phase Voltage BN | float32 | V |  | Phase Voltage BN |  | M
17 | 18 | 2 | R | PhVphC | Phase Voltage CN | float32 | V |  | Phase Voltage CN |  | M
19 | 20 | 2 | R | PPV | Voltage LL | float32 | V |  | Line to Line AC Voltage (average of active phases) |  | M
21 | 22 | 2 | R | PPVphAB | Phase Voltage AB | float32 | V |  | Phase Voltage AB |  | M
23 | 24 | 2 | R | PPVphBC | Phase Voltage BC | float32 | V |  | Phase Voltage BC |  | M
25 | 26 | 2 | R | PPVphCA | Phase Voltage CA | float32 | V |  | Phase Voltage CA |  | M
27 | 28 | 2 | R | Hz | Hz | float32 | Hz |  | Frequency |  | M
29 | 30 | 2 | R | W | Watts | float32 | W |  | Total Real Power |  | M
31 | 32 | 2 | R | WphA | Watts phase A | float32 | W |  |  |  | O
33 | 34 | 2 | R | WphB | Watts phase B | float32 | W |  |  |  | O
35 | 36 | 2 | R | WphC | Watts phase C | float32 | W |  |  |  | O
37 | 38 | 2 | R | VA | VA | float32 | VA |  | AC Apparent Power |  | O
39 | 40 | 2 | R | VAphA | VA phase A | float32 | VA |  |  |  | O
41 | 42 | 2 | R | VAphB | VA phase B | float32 | VA |  |  |  | O
43 | 44 | 2 | R | VAphC | VA phase C | float32 | VA |  |  |  | O
45 | 46 | 2 | R | VAR | VAR | float32 | var |  | Reactive Power |  | O
47 | 48 | 2 | R | VARphA | VAR phase A | float32 | var |  |  |  | O
49 | 50 | 2 | R | VARphB | VAR phase B | float32 | var |  |  |  | O
51 | 52 | 2 | R | VARphC | VAR phase C | float32 | var |  |  |  | O
53 | 54 | 2 | R | PF | PF | float32 | PF |  | Power Factor |  | O
55 | 56 | 2 | R | PFphA | PF phase A | float32 | PF |  |  |  | O
57 | 58 | 2 | R | PFphB | PF phase B | float32 | PF |  |  |  | O
59 | 60 | 2 | R | PFphC | PF phase C | float32 | PF |  |  |  | O
61 | 62 | 2 | R | TotWhExp | Total Watt-hours Exported | acc32 | Wh |  | Total Real Energy Exported |  | M
63 | 64 | 2 | R | TotWhExpPhA | Total Watt-hours Exported phase A | acc32 | Wh |  |  |  | O
65 | 66 | 2 | R | TotWhExpPhB | Total Watt-hours Exported phase B | acc32 | Wh |  |  |  | O
67 | 68 | 2 | R | TotWhExpPhC | Total Watt-hours Exported phase C | acc32 | Wh |  |  |  | O
69 | 70 | 2 | R | TotWhImp | Total Watt-hours Imported | acc32 | Wh |  | Total Real Energy Imported |  | M
71 | 72 | 2 | R | TotWhImpPhA | Total Watt-hours Imported phase A | acc32 | Wh |  |  |  | O
73 | 74 | 2 | R | TotWhImpPhB | Total Watt-hours Imported phase B | acc32 | Wh |  |  |  | O
75 | 76 | 2 | R | TotWhImpPhC | Total Watt-hours Imported phase C | acc32 | Wh |  |  |  | O
77 | 78 | 2 | R | TotVAhExp | Total VA-hours Exported | acc32 | VAh |  | Total Apparent Energy Exported |  | O
79 | 80 | 2 | R | TotVAhExpPhA | Total VA-hours Exported phase A | acc32 | VAh |  |  |  | O
81 | 82 | 2 | R | TotVAhExpPhB | Total VA-hours Exported phase B | acc32 | VAh |  |  |  | O
83 | 84 | 2 | R | TotVAhExpPhC | Total VA-hours Exported phase C | acc32 | VAh |  |  |  | O
85 | 86 | 2 | R | TotVAhImp | Total VA-hours Imported | acc32 | VAh |  | Total Apparent Energy Imported |  | O
87 | 88 | 2 | R | TotVAhImpPhA | Total VA-hours Imported phase A | acc32 | VAh |  |  |  | O
89 | 90 | 2 | R | TotVAhImpPhB | Total VA-hours Imported phase B | acc32 | VAh |  |  |  | O
91 | 92 | 2 | R | TotVAhImpPhC | Total VA-hours Imported phase C | acc32 | VAh |  |  |  | O
93 | 94 | 2 | R | TotVArhImpQ1 | Total VAR-hours Imported Q1 | acc32 | varh |  | Total Reactive Energy Imported Quadrant 1 |  | O
95 | 96 | 2 | R | TotVArhImpQ1phA |  | acc32 | varh |  |  |  | O
97 | 98 | 2 | R | TotVArhImpQ1phB |  | acc32 | varh |  |  |  | O
99 | 100 | 2 | R | TotVArhImpQ1phC |  | acc32 | varh |  |  |  | O
101 | 102 | 2 | R | TotVArhImpQ2 | Total VAr-hours Imported Q2 | acc32 | varh |  | Total Reactive Power Imported Quadrant 2 |  | O
103 | 104 | 2 | R | TotVArhImpQ2phA |  | acc32 | varh |  |  |  | O
105 | 106 | 2 | R | TotVArhImpQ2phB |  | acc32 | varh |  |  |  | O
107 | 108 | 2 | R | TotVArhImpQ2phC |  | acc32 | varh |  |  |  | O
109 | 110 | 2 | R | TotVArhExpQ3 | Total VAr-hours Exported Q3 | acc32 | varh |  | Total Reactive Power Exported Quadrant 3 |  | O
111 | 112 | 2 | R | TotVArhExpQ3phA |  | acc32 | varh |  |  |  | O
113 | 114 | 2 | R | TotVArhExpQ3phB |  | acc32 | varh |  |  |  | O
115 | 116 | 2 | R | TotVArhExpQ3phC |  | acc32 | varh |  |  |  | O
117 | 118 | 2 | R | TotVArhExpQ4 | Total VAr-hours Exported Q4 | acc32 | varh |  | Total Reactive Power Exported Quadrant 4 |  | O
119 | 120 | 2 | R | TotVArhExpQ4phA |  | acc32 | varh |  |  |  | O
121 | 122 | 2 | R | TotVArhExpQ4phB |  | acc32 | varh |  |  |  | O
123 | 124 | 2 | R | TotVArhExpQ4phC |  | acc32 | varh |  |  |  | O
125 | 126 | 2 | R | Evt | Events | bitfield32 |  |  | Meter Event Flags |  | M
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
M_EVENT_Power_Failure |  |  | 2
M_EVENT_Under_Voltage |  |  | 3
M_EVENT_Low_PF |  |  | 4
M_EVENT_Over_Current |  |  | 5
M_EVENT_Over_Voltage |  |  | 6
M_EVENT_Missing_Sensor |  |  | 7
M_EVENT_Reserved1 |  |  | 8
M_EVENT_Reserved2 |  |  | 9
M_EVENT_Reserved3 |  |  | 10
M_EVENT_Reserved4 |  |  | 11
M_EVENT_Reserved5 |  |  | 12
M_EVENT_Reserved6 |  |  | 13
M_EVENT_Reserved7 |  |  | 14
M_EVENT_Reserved8 |  |  | 15
M_EVENT_OEM01 |  |  | 16
M_EVENT_OEM02 |  |  | 17
M_EVENT_OEM03 |  |  | 18
M_EVENT_OEM04 |  |  | 19
M_EVENT_OEM05 |  |  | 20
M_EVENT_OEM06 |  |  | 21
M_EVENT_OEM07 |  |  | 22
M_EVENT_OEM08 |  |  | 23
M_EVENT_OEM09 |  |  | 24
M_EVENT_OEM10 |  |  | 25
M_EVENT_OEM11 |  |  | 26
M_EVENT_OEM12 |  |  | 27
M_EVENT_OEM13 |  |  | 28
M_EVENT_OEM14 |  |  | 29
M_EVENT_OEM15 |  |  | 30

## M 214
// 214-delta-connect three phase (abc) meter : (Float)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 214. Uniquely identifies this as a SunSpec delta-connect three phase (abc) meter Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 124 |  | M
// 214 delta-connect three phase (abc) meter Fixed Block (124)
3 | 4 | 2 | R | A | Amps | float32 | A |  | Total AC Current |  | M
5 | 6 | 2 | R | AphA | Amps PhaseA | float32 | A |  | Phase A Current |  | M
7 | 8 | 2 | R | AphB | Amps PhaseB | float32 | A |  | Phase B Current |  | M
9 | 10 | 2 | R | AphC | Amps PhaseC | float32 | A |  | Phase C Current |  | M
11 | 12 | 2 | R | PhV | Voltage LN | float32 | V |  | Line to Neutral AC Voltage (average of active phases) |  | O
13 | 14 | 2 | R | PhVphA | Phase Voltage AN | float32 | V |  | Phase Voltage AN |  | O
15 | 16 | 2 | R | PhVphB | Phase Voltage BN | float32 | V |  | Phase Voltage BN |  | O
17 | 18 | 2 | R | PhVphC | Phase Voltage CN | float32 | V |  | Phase Voltage CN |  | O
19 | 20 | 2 | R | PPV | Voltage LL | float32 | V |  | Line to Line AC Voltage (average of active phases) |  | M
21 | 22 | 2 | R | PPVphAB | Phase Voltage AB | float32 | V |  | Phase Voltage AB |  | M
23 | 24 | 2 | R | PPVphBC | Phase Voltage BC | float32 | V |  | Phase Voltage BC |  | M
25 | 26 | 2 | R | PPVphCA | Phase Voltage CA | float32 | V |  | Phase Voltage CA |  | M
27 | 28 | 2 | R | Hz | Hz | float32 | Hz |  | Frequency |  | M
29 | 30 | 2 | R | W | Watts | float32 | W |  | Total Real Power |  | M
31 | 32 | 2 | R | WphA | Watts phase A | float32 | W |  |  |  | O
33 | 34 | 2 | R | WphB | Watts phase B | float32 | W |  |  |  | O
35 | 36 | 2 | R | WphC | Watts phase C | float32 | W |  |  |  | O
37 | 38 | 2 | R | VA | VA | float32 | VA |  | AC Apparent Power |  | O
39 | 40 | 2 | R | VAphA | VA phase A | float32 | VA |  |  |  | O
41 | 42 | 2 | R | VAphB | VA phase B | float32 | VA |  |  |  | O
43 | 44 | 2 | R | VAphC | VA phase C | float32 | VA |  |  |  | O
45 | 46 | 2 | R | VAR | VAR | float32 | var |  | Reactive Power |  | O
47 | 48 | 2 | R | VARphA | VAR phase A | float32 | var |  |  |  | O
49 | 50 | 2 | R | VARphB | VAR phase B | float32 | var |  |  |  | O
51 | 52 | 2 | R | VARphC | VAR phase C | float32 | var |  |  |  | O
53 | 54 | 2 | R | PF | PF | float32 | PF |  | Power Factor |  | O
55 | 56 | 2 | R | PFphA | PF phase A | float32 | PF |  |  |  | O
57 | 58 | 2 | R | PFphB | PF phase B | float32 | PF |  |  |  | O
59 | 60 | 2 | R | PFphC | PF phase C | float32 | PF |  |  |  | O
61 | 62 | 2 | R | TotWhExp | Total Watt-hours Exported | acc32 | Wh |  | Total Real Energy Exported |  | M
63 | 64 | 2 | R | TotWhExpPhA | Total Watt-hours Exported phase A | acc32 | Wh |  |  |  | O
65 | 66 | 2 | R | TotWhExpPhB | Total Watt-hours Exported phase B | acc32 | Wh |  |  |  | O
67 | 68 | 2 | R | TotWhExpPhC | Total Watt-hours Exported phase C | acc32 | Wh |  |  |  | O
69 | 70 | 2 | R | TotWhImp | Total Watt-hours Imported | acc32 | Wh |  | Total Real Energy Imported |  | M
71 | 72 | 2 | R | TotWhImpPhA | Total Watt-hours Imported phase A | acc32 | Wh |  |  |  | O
73 | 74 | 2 | R | TotWhImpPhB | Total Watt-hours Imported phase B | acc32 | Wh |  |  |  | O
75 | 76 | 2 | R | TotWhImpPhC | Total Watt-hours Imported phase C | acc32 | Wh |  |  |  | O
77 | 78 | 2 | R | TotVAhExp | Total VA-hours Exported | acc32 | VAh |  | Total Apparent Energy Exported |  | O
79 | 80 | 2 | R | TotVAhExpPhA | Total VA-hours Exported phase A | acc32 | VAh |  |  |  | O
81 | 82 | 2 | R | TotVAhExpPhB | Total VA-hours Exported phase B | acc32 | VAh |  |  |  | O
83 | 84 | 2 | R | TotVAhExpPhC | Total VA-hours Exported phase C | acc32 | VAh |  |  |  | O
85 | 86 | 2 | R | TotVAhImp | Total VA-hours Imported | acc32 | VAh |  | Total Apparent Energy Imported |  | O
87 | 88 | 2 | R | TotVAhImpPhA | Total VA-hours Imported phase A | acc32 | VAh |  |  |  | O
89 | 90 | 2 | R | TotVAhImpPhB | Total VA-hours Imported phase B | acc32 | VAh |  |  |  | O
91 | 92 | 2 | R | TotVAhImpPhC | Total VA-hours Imported phase C | acc32 | VAh |  |  |  | O
93 | 94 | 2 | R | TotVArhImpQ1 | Total VAR-hours Imported Q1 | acc32 | varh |  | Total Reactive Energy Imported Quadrant 1 |  | O
95 | 96 | 2 | R | TotVArhImpQ1phA |  | acc32 | varh |  |  |  | O
97 | 98 | 2 | R | TotVArhImpQ1phB |  | acc32 | varh |  |  |  | O
99 | 100 | 2 | R | TotVArhImpQ1phC |  | acc32 | varh |  |  |  | O
101 | 102 | 2 | R | TotVArhImpQ2 | Total VAr-hours Imported Q2 | acc32 | varh |  | Total Reactive Power Imported Quadrant 2 |  | O
103 | 104 | 2 | R | TotVArhImpQ2phA |  | acc32 | varh |  |  |  | O
105 | 106 | 2 | R | TotVArhImpQ2phB |  | acc32 | varh |  |  |  | O
107 | 108 | 2 | R | TotVArhImpQ2phC |  | acc32 | varh |  |  |  | O
109 | 110 | 2 | R | TotVArhExpQ3 | Total VAr-hours Exported Q3 | acc32 | varh |  | Total Reactive Power Exported Quadrant 3 |  | O
111 | 112 | 2 | R | TotVArhExpQ3phA |  | acc32 | varh |  |  |  | O
113 | 114 | 2 | R | TotVArhExpQ3phB |  | acc32 | varh |  |  |  | O
115 | 116 | 2 | R | TotVArhExpQ3phC |  | acc32 | varh |  |  |  | O
117 | 118 | 2 | R | TotVArhExpQ4 | Total VAr-hours Exported Q4 | acc32 | varh |  | Total Reactive Power Exported Quadrant 4 |  | O
119 | 120 | 2 | R | TotVArhExpQ4phA |  | acc32 | varh |  |  |  | O
121 | 122 | 2 | R | TotVArhExpQ4phB |  | acc32 | varh |  |  |  | O
123 | 124 | 2 | R | TotVArhExpQ4phC |  | acc32 | varh |  |  |  | O
125 | 126 | 2 | R | Evt | Events | bitfield32 |  |  | Meter Event Flags |  | M
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
M_EVENT_Power_Failure |  |  | 2
M_EVENT_Under_Voltage |  |  | 3
M_EVENT_Low_PF |  |  | 4
M_EVENT_Over_Current |  |  | 5
M_EVENT_Over_Voltage |  |  | 6
M_EVENT_Missing_Sensor |  |  | 7
M_EVENT_Reserved1 |  |  | 8
M_EVENT_Reserved2 |  |  | 9
M_EVENT_Reserved3 |  |  | 10
M_EVENT_Reserved4 |  |  | 11
M_EVENT_Reserved5 |  |  | 12
M_EVENT_Reserved6 |  |  | 13
M_EVENT_Reserved7 |  |  | 14
M_EVENT_Reserved8 |  |  | 15
M_EVENT_OEM01 |  |  | 16
M_EVENT_OEM02 |  |  | 17
M_EVENT_OEM03 |  |  | 18
M_EVENT_OEM04 |  |  | 19
M_EVENT_OEM05 |  |  | 20
M_EVENT_OEM06 |  |  | 21
M_EVENT_OEM07 |  |  | 22
M_EVENT_OEM08 |  |  | 23
M_EVENT_OEM09 |  |  | 24
M_EVENT_OEM10 |  |  | 25
M_EVENT_OEM11 |  |  | 26
M_EVENT_OEM12 |  |  | 27
M_EVENT_OEM13 |  |  | 28
M_EVENT_OEM14 |  |  | 29
M_EVENT_OEM15 |  |  | 30

## E 302
// 302-Irradiance Model : Include to support various irradiance measurements ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 302. Uniquely identifies this as a SunSpec Irradiance Model Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 5 |  | M
// 302 Irradiance Model Fixed Block (5)
3 | 3 | 1 | R | GHI | GHI | uint16 | W/m2 |  | Global Horizontal Irradiance |  | O
4 | 4 | 1 | R | POAI | POAI | uint16 | W/m2 |  | Plane-of-Array Irradiance |  | O
5 | 5 | 1 | R | DFI | DFI | uint16 | W/m2 |  | Diffuse Irradiance |  | O
6 | 6 | 1 | R | DNI | DNI | uint16 | W/m2 |  | Direct Normal Irradiance |  | O
7 | 7 | 1 | R | OTI | OTI | uint16 | W/m2 |  | Other Irradiance |  | O

## E 303
// 303-Back of Module Temperature Model : Include to support variable number of back of module temperature measurements ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 303. Uniquely identifies this as a SunSpec Back of Module Temperature Model Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : N*1 |  | M
// 303 Back of Module Temperature Model Repeating Block (1)
3 | 3 | 1 | R | TmpBOM | Temp | int16 | C | -1 | Back of module temperature measurement |  | M

## E 304
// 304-Inclinometer Model : Include to support orienation measurements ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 304. Uniquely identifies this as a SunSpec Inclinometer Model Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : N*6 |  | M
// 304 Inclinometer Model Repeating Block (6)
3 | 4 | 2 | R | Inclx | X | int32 | Degrees | -2 | X-Axis inclination |  | M
5 | 6 | 2 | R | Incly | Y | int32 | Degrees | -2 | Y-Axis inclination |  | O
7 | 8 | 2 | R | Inclz | Z | int32 | Degrees | -2 | Z-Axis inclination |  | O

## E 305
// 305-GPS : Include to support location measurements ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 305. Uniquely identifies this as a SunSpec GPS Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 36 |  | M
// 305 GPS Fixed Block (36)
3 | 8 | 6 | R | Tm | Tm | string | hhmmss.sssZ |  | UTC 24 hour time stamp to millisecond hhmmss.sssZ format |  | O
9 | 12 | 4 | R | Date | Date | string | YYYYMMDD |  | UTC Date string YYYYMMDD format |  | O
13 | 32 | 20 | R | Loc | Location | string | text |  | Location string (40 chars max) |  | O
33 | 34 | 2 | R | Lat | Lat | int32 | Degrees | -7 | Lattitude with seven degrees of precision |  | O
35 | 36 | 2 | R | Long | Long | int32 | Degrees | -7 | Longitude with seven degrees of precision |  | O
37 | 38 | 2 | R | Alt | Altitude | int32 | meters |  | Altitude measurement in meters |  | O

## E 306
// 306-Reference Point Model : Include to support a standard reference point ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 306. Uniquely identifies this as a SunSpec Reference Point Model Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 4 |  | M
// 306 Reference Point Model Fixed Block (4)
3 | 3 | 1 | R | GHI | GHI | uint16 | W/m2 |  | Global Horizontal Irrandiance |  | O
4 | 4 | 1 | R | A | Amps | uint16 | W/m2 |  | Current measurment at reference point |  | O
5 | 5 | 1 | R | V | Voltage | uint16 | W/m2 |  | Voltage measurment at reference point |  | O
6 | 6 | 1 | R | Tmp | Temperature | uint16 | W/m2 |  | Temperature measurment at reference point |  | O

## E 307
// 307-Base Met : Base Meteorolgical Model (This model supersedes model 301)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 307. Uniquely identifies this as a SunSpec Base Met Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 11 |  | M
// 307 Base Met Fixed Block (11)
3 | 3 | 1 | R | TmpAmb | Ambient Temperature | int16 | C | -1 |  |  | O
4 | 4 | 1 | R | RH | Relative Humidity | int16 | Pct |  |  |  | O
5 | 5 | 1 | R | Pres | Barometric Pressure | int16 | HPa |  |  |  | O
6 | 6 | 1 | R | WndSpd | Wind Speed | int16 | mps |  |  |  | O
7 | 7 | 1 | R | WndDir | Wind Direction | int16 | deg |  |  |  | O
8 | 8 | 1 | R | Rain | Rainfall | int16 | mm |  |  |  | O
9 | 9 | 1 | R | Snw | Snow Depth | int16 | mm |  |  |  | O
10 | 10 | 1 | R | PPT | Precipitation Type | int16 |  |  | �Precipitation Type (WMO 4680 SYNOP code reference) |  | O
11 | 11 | 1 | R | ElecFld | Electric Field | int16 | Vm |  |  |  | O
12 | 12 | 1 | R | SurWet | Surface Wetness | int16 | kO |  |  |  | O
13 | 13 | 1 | R | SoilWet | Soil Wetness | int16 | Pct |  |  |  | O

## E 308
// 308-Mini Met Model : Include to support a few basic measurements ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 308. Uniquely identifies this as a SunSpec Mini Met Model Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 4 |  | M
// 308 Mini Met Model Fixed Block (4)
3 | 3 | 1 | R | GHI | GHI | uint16 | W/m2 |  | Global Horizontal Irradiance |  | O
4 | 4 | 1 | R | TmpBOM | Temp | int16 | C | -1 | Back of module temperature measurement |  | O
5 | 5 | 1 | R | TmpAmb | Ambient Temperature | int16 | C | -1 |  |  | O
6 | 6 | 1 | R | WndSpd | Wind Speed | uint16 | m/s |  |  |  | O

## SC 401
// 401-String Combiner (Current) : A basic string combiner (This model is SUPERSEDED by model 403)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 401. Uniquely identifies this as a SunSpec String Combiner (Current) Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 14+N*8 |  | M
// 401 String Combiner (Current) Fixed Block (14)
3 | 3 | 1 | R | DCA_SF |  | sunssf |  |  | Current scale factor |  | M
4 | 4 | 1 | R | DCAhr_SF |  | sunssf |  |  | Amp-hour scale factor |  | O
5 | 5 | 1 | R | DCV_SF |  | sunssf |  |  | Voltage scale factor |  | O
6 | 6 | 1 | R | DCAMax | Rating | uint16 | A | DCA_SF | Maximum DC Current Rating |  | M
7 | 7 | 1 | R | N | N | uint16 |  |  | Number of Inputs |  | M
8 | 9 | 2 | R | Evt | Event | bitfield32 |  |  | Bitmask value. Events |  | M
10 | 11 | 2 | R | EvtVnd | Vendor Event | bitfield32 |  |  | Bitmask value. Vendor defnied events |  | O
12 | 12 | 1 | R | DCA | Amps | int16 | A | DCA_SF | Total measured current |  | M
13 | 14 | 2 | R | DCAhr | Amp-hours | uint32 | Ah | DCAhr_SF | Total metered Amp-hours |  | O
15 | 15 | 1 | R | DCV | Voltage | uint16 | V | DCV_SF | Output Voltage |  | O
16 | 16 | 1 | R | Tmp | Temp | int16 | C |  | Internal operating temperature |  | O
// 401 String Combiner (Current) Repeating Block (8)
17 | 17 | 1 | R | InID | ID | uint16 |  |  | Uniquely identifies this input set |  | M
18 | 19 | 2 | R | InEvt | Event | bitfield32 |  |  | String Input Event Flags |  | M
20 | 21 | 2 | R | InEvtVnd | Vendor Event | bitfield32 |  |  | String Input Vendor Event Flags |  | O
22 | 22 | 1 | R | InDCA | Amps | int16 | A | DCA_SF | String Input Current |  | M
23 | 24 | 2 | R | InDCAhr | Amp-hours | uint32 | Ah | DCAhr_SF | String Input Amp-Hours |  | O
// InEvt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
LOW_VOLTAGE |  |  | 0
LOW_POWER |  |  | 1
LOW_EFFICIENCY |  |  | 2
CURRENT |  |  | 3
VOLTAGE |  |  | 4
POWER |  |  | 5
PR |  |  | 6
DISCONNECTED |  |  | 7
FUSE_FAULT |  |  | 8
COMBINER_FUSE_FAULT |  |  | 9
COMBINER_CABINET_OPEN |  |  | 10
TEMP |  |  | 11
GROUNDFAULT |  |  | 12
REVERSED_POLARITY |  |  | 13
INCOMPATIBLE |  |  | 14
COMM_ERROR |  |  | 15
INTERNAL_ERROR |  |  | 16
THEFT |  |  | 17
ARC_DETECTED |  |  | 18
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
LOW_VOLTAGE |  |  | 0
LOW_POWER |  |  | 1
LOW_EFFICIENCY |  |  | 2
CURRENT |  |  | 3
VOLTAGE |  |  | 4
POWER |  |  | 5
PR |  |  | 6
DISCONNECTED |  |  | 7
FUSE_FAULT |  |  | 8
COMBINER_FUSE_FAULT |  |  | 9
COMBINER_CABINET_OPEN |  |  | 10
TEMP |  |  | 11
GROUNDFAULT |  |  | 12
REVERSED_POLARITY |  |  | 13
INCOMPATIBLE |  |  | 14
COMM_ERROR |  |  | 15
INTERNAL_ERROR |  |  | 16
THEFT |  |  | 17
ARC_DETECTED |  |  | 18

## SC 402
// 402-String Combiner (Advanced) : An advanced string combiner (This model is SUPERSEDED by model 404)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 402. Uniquely identifies this as a SunSpec String Combiner (Advanced) Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 20+N*14 |  | M
// 402 String Combiner (Advanced) Fixed Block (20)
3 | 3 | 1 | R | DCA_SF |  | sunssf |  |  | Current scale factor |  | M
4 | 4 | 1 | R | DCAhr_SF |  | sunssf |  |  | Amp-hour scale factor |  | O
5 | 5 | 1 | R | DCV_SF |  | sunssf |  |  | Voltage scale factor |  | O
6 | 6 | 1 | R | DCW_SF |  | sunssf |  |  | Power scale factor |  | O
7 | 7 | 1 | R | DCWh_SF |  | sunssf |  |  | Energy scale factor |  | M
8 | 8 | 1 | R | DCAMax | Rating | uint16 | A |  | Maximum DC Current Rating |  | O
9 | 9 | 1 | R | N | N | uint16 |  |  | Number of Inputs |  | O
10 | 11 | 2 | R | Evt | Event | bitfield32 |  |  | Bitmask value. Events |  | M
12 | 13 | 2 | R | EvtVnd | Vendor Event | bitfield32 |  |  | Bitmask value. Vendor defnied events |  | O
14 | 14 | 1 | R | DCA | Amps | int16 | A | DCA_SF | Total measured current |  | M
15 | 16 | 2 | R | DCAhr | Amp-hours | uint32 | Ah | DCAhr_SF | Total metered Amp-hours |  | O
17 | 17 | 1 | R | DCV | Voltage | uint16 | V | DCV_SF | Output Voltage |  | O
18 | 18 | 1 | R | Tmp | Temp | int16 | C |  | Internal operating temperature |  | O
19 | 19 | 1 | R | DCW | Watts | int16 | W | DCW_SF | Output power |  | O
20 | 20 | 1 | R | DCPR | PR | uint16 | Pct |  | DC Performance ratio value |  | O
21 | 22 | 2 | R | DCWh | Watt-hours | uint32 | Wh | DCWh_SF | Output energy |  | M
// 402 String Combiner (Advanced) Repeating Block (14)
23 | 23 | 1 | R | InID | ID | uint16 |  |  | Uniquely identifies this input set |  | M
24 | 25 | 2 | R | InEvt | Event | bitfield32 |  |  | String Input Event Flags |  | M
26 | 27 | 2 | R | EvtVnd | Vendor Event | bitfield32 |  |  | Bitmask value. Vendor defnied events |  | O
28 | 28 | 1 | R | InDCA | Amps | int16 | A | DCA_SF | String Input Current |  | M
29 | 30 | 2 | R | InDCAhr | Amp-hours | uint32 | Ah | DCAhr_SF | String Input Amp-Hours |  | O
31 | 31 | 1 | R | InDCV | Voltage | uint16 | V | DCV_SF | String Input Voltage |  | O
32 | 32 | 1 | R | InDCW | Watts | int16 | W | DCWh_SF | String Input Power |  | O
33 | 34 | 2 | R | InDCWh | Watt-hours | uint32 | Wh |  | String Input Energy |  | O
35 | 35 | 1 | R | InDCPR | PR | uint16 | Pct |  | String Performance Ratio |  | O
36 | 36 | 1 | R | InN | N | uint16 |  |  | Number of modules in this input string | Configured value | O
// InEvt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
LOW_VOLTAGE |  |  | 0
LOW_POWER |  |  | 1
LOW_EFFICIENCY |  |  | 2
CURRENT |  |  | 3
VOLTAGE |  |  | 4
POWER |  |  | 5
PR |  |  | 6
DISCONNECTED |  |  | 7
FUSE_FAULT |  |  | 8
COMBINER_FUSE_FAULT |  |  | 9
COMBINER_CABINET_OPEN |  |  | 10
TEMP |  |  | 11
GROUNDFAULT |  |  | 12
REVERSED_POLARITY |  |  | 13
INCOMPATIBLE |  |  | 14
COMM_ERROR |  |  | 15
INTERNAL_ERROR |  |  | 16
THEFT |  |  | 17
ARC_DETECTED |  |  | 18
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
LOW_VOLTAGE |  |  | 0
LOW_POWER |  |  | 1
LOW_EFFICIENCY |  |  | 2
CURRENT |  |  | 3
VOLTAGE |  |  | 4
POWER |  |  | 5
PR |  |  | 6
DISCONNECTED |  |  | 7
FUSE_FAULT |  |  | 8
COMBINER_FUSE_FAULT |  |  | 9
COMBINER_CABINET_OPEN |  |  | 10
TEMP |  |  | 11
GROUNDFAULT |  |  | 12
REVERSED_POLARITY |  |  | 13
INCOMPATIBLE |  |  | 14
COMM_ERROR |  |  | 15
INTERNAL_ERROR |  |  | 16
THEFT |  |  | 17
ARC_DETECTED |  |  | 18

## SC 403
// 403-String Combiner (Current) : A basic string combiner model (This model supersedes model 401)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 403. Uniquely identifies this as a SunSpec String Combiner (Current) Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 16+N*8 |  | M
// 403 String Combiner (Current) Fixed Block (16)
3 | 3 | 1 | R | DCA_SF |  | sunssf |  |  | Current scale factor |  | M
4 | 4 | 1 | R | DCAhr_SF |  | sunssf |  |  | Amp-hour scale factor |  | O
5 | 5 | 1 | R | DCV_SF |  | sunssf |  |  | Voltage scale factor |  | O
6 | 6 | 1 | R | DCAMax | Rating | uint16 | A | DCA_SF | Maximum DC Current Rating |  | M
7 | 7 | 1 | R | N | N | uint16 |  |  | Number of Inputs |  | M
8 | 9 | 2 | R | Evt | Event | bitfield32 |  |  | Bitmask value. Events |  | M
10 | 11 | 2 | R | EvtVnd | Vendor Event | bitfield32 |  |  | Bitmask value. Vendor defnied events |  | O
12 | 12 | 1 | R | DCA | Amps | int16 | A | DCA_SF | Total measured current |  | M
13 | 14 | 2 | R | DCAhr | Amp-hours | acc32 | Ah | DCAhr_SF | Total metered Amp-hours |  | O
15 | 15 | 1 | R | DCV | Voltage | int16 | V | DCV_SF | Output Voltage |  | O
16 | 16 | 1 | R | Tmp | Temp | int16 | C |  | Internal operating temperature |  | O
17 | 17 | 1 | R | InDCA_SF |  | sunssf |  |  | Current scale factor for inputs |  | O
18 | 18 | 1 | R | InDCAhr_SF |  | sunssf |  |  | Amp-hour scale factor for inputs |  | O
// 403 String Combiner (Current) Repeating Block (8)
19 | 19 | 1 | R | InID | ID | uint16 |  |  | Uniquely identifies this input set |  | M
20 | 21 | 2 | R | InEvt | Event | bitfield32 |  |  | String Input Event Flags |  | M
22 | 23 | 2 | R | InEvtVnd | Vendor Event | bitfield32 |  |  | String Input Vendor Event Flags |  | O
24 | 24 | 1 | R | InDCA | Amps | int16 | A | InDCA_SF | String Input Current |  | M
25 | 26 | 2 | R | InDCAhr | Amp-hours | acc32 | Ah | InDCAhr_SF | String Input Amp-Hours |  | O
// InEvt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
LOW_VOLTAGE |  |  | 0
LOW_POWER |  |  | 1
LOW_EFFICIENCY |  |  | 2
CURRENT |  |  | 3
VOLTAGE |  |  | 4
POWER |  |  | 5
PR |  |  | 6
DISCONNECTED |  |  | 7
FUSE_FAULT |  |  | 8
COMBINER_FUSE_FAULT |  |  | 9
COMBINER_CABINET_OPEN |  |  | 10
TEMP |  |  | 11
GROUNDFAULT |  |  | 12
REVERSED_POLARITY |  |  | 13
INCOMPATIBLE |  |  | 14
COMM_ERROR |  |  | 15
INTERNAL_ERROR |  |  | 16
THEFT |  |  | 17
ARC_DETECTED |  |  | 18
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
LOW_VOLTAGE |  |  | 0
LOW_POWER |  |  | 1
LOW_EFFICIENCY |  |  | 2
CURRENT |  |  | 3
VOLTAGE |  |  | 4
POWER |  |  | 5
PR |  |  | 6
DISCONNECTED |  |  | 7
FUSE_FAULT |  |  | 8
COMBINER_FUSE_FAULT |  |  | 9
COMBINER_CABINET_OPEN |  |  | 10
TEMP |  |  | 11
GROUNDFAULT |  |  | 12
REVERSED_POLARITY |  |  | 13
INCOMPATIBLE |  |  | 14
COMM_ERROR |  |  | 15
INTERNAL_ERROR |  |  | 16
THEFT |  |  | 17
ARC_DETECTED |  |  | 18

## SC 404
// 404-String Combiner (Advanced) : An advanced string combiner including voltage and energy measurements (This model supersedes model 402)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 404. Uniquely identifies this as a SunSpec String Combiner (Advanced) Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 25+N*14 |  | M
// 404 String Combiner (Advanced) Fixed Block (25)
3 | 3 | 1 | R | DCA_SF |  | sunssf |  |  | Current scale factor |  | M
4 | 4 | 1 | R | DCAhr_SF |  | sunssf |  |  | Amp-hour scale factor |  | O
5 | 5 | 1 | R | DCV_SF |  | sunssf |  |  | Voltage scale factor |  | O
6 | 6 | 1 | R | DCW_SF |  | sunssf |  |  | Power scale factor |  | O
7 | 7 | 1 | R | DCWh_SF |  | sunssf |  |  | Energy scale factor |  | O
8 | 8 | 1 | R | DCAMax | Rating | uint16 | A | DCA_SF | Maximum DC Current Rating |  | M
9 | 9 | 1 | R | N | N | uint16 |  |  | Number of Inputs |  | M
10 | 11 | 2 | R | Evt | Event | bitfield32 |  |  | Bitmask value. Events |  | M
12 | 13 | 2 | R | EvtVnd | Vendor Event | bitfield32 |  |  | Bitmask value. Vendor defnied events |  | O
14 | 14 | 1 | R | DCA | Amps | int16 | A | DCA_SF | Total measured current |  | M
15 | 16 | 2 | R | DCAhr | Amp-hours | acc32 | Ah | DCAhr_SF | Total metered Amp-hours |  | O
17 | 17 | 1 | R | DCV | Voltage | int16 | V | DCV_SF | Output Voltage |  | O
18 | 18 | 1 | R | Tmp | Temp | int16 | C |  | Internal operating temperature |  | O
19 | 19 | 1 | R | DCW | Watts | int16 | W | DCW_SF | Output power |  | O
20 | 20 | 1 | R | DCPR | PR | int16 | Pct |  | DC Performance ratio value |  | O
21 | 22 | 2 | R | DCWh | Watt-hours | acc32 | Wh | DCWh_SF | Output energy |  | O
23 | 23 | 1 | R | InDCA_SF |  | sunssf |  |  | Current scale factor for inputs |  | O
24 | 24 | 1 | R | InDCAhr_SF |  | sunssf |  |  | Amp-hour scale factor for inputs |  | O
25 | 25 | 1 | R | InDCV_SF |  | sunssf |  |  | Voltage scale factor for inputs |  | O
26 | 26 | 1 | R | InDCW_SF |  | sunssf |  |  | Power scale factor for inputs |  | O
27 | 27 | 1 | R | InDCWh_SF |  | sunssf |  |  | Energy scale factor for inputs |  | O
// 404 String Combiner (Advanced) Repeating Block (14)
28 | 28 | 1 | R | InID | ID | uint16 |  |  | Uniquely identifies this input set |  | M
29 | 30 | 2 | R | InEvt | Event | bitfield32 |  |  | String Input Event Flags |  | M
31 | 32 | 2 | R | InEvtVnd | Vendor Event | bitfield32 |  |  | String Input Vendor Event Flags |  | O
33 | 33 | 1 | R | InDCA | Amps | int16 | A | InDCA_SF | String Input Current |  | M
34 | 35 | 2 | R | InDCAhr | Amp-hours | acc32 | Ah | InDCAhr_SF | String Input Amp-Hours |  | O
36 | 36 | 1 | R | InDCV | Voltage | int16 | V | InDCV_SF | String Input Voltage |  | O
37 | 37 | 1 | R | InDCW | Watts | int16 | W | InDCW_SF | String Input Power |  | O
38 | 39 | 2 | R | InDCWh | Watt-hours | acc32 | Wh | InDCWh_SF | String Input Energy |  | O
40 | 40 | 1 | R | InDCPR | PR | uint16 | Pct |  | String Performance Ratio |  | O
41 | 41 | 1 | R | InN | N | uint16 |  |  | Number of modules in this input string | Configured value | O
// InEvt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
LOW_VOLTAGE |  |  | 0
LOW_POWER |  |  | 1
LOW_EFFICIENCY |  |  | 2
CURRENT |  |  | 3
VOLTAGE |  |  | 4
POWER |  |  | 5
PR |  |  | 6
DISCONNECTED |  |  | 7
FUSE_FAULT |  |  | 8
COMBINER_FUSE_FAULT |  |  | 9
COMBINER_CABINET_OPEN |  |  | 10
TEMP |  |  | 11
GROUNDFAULT |  |  | 12
REVERSED_POLARITY |  |  | 13
INCOMPATIBLE |  |  | 14
COMM_ERROR |  |  | 15
INTERNAL_ERROR |  |  | 16
THEFT |  |  | 17
ARC_DETECTED |  |  | 18
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
LOW_VOLTAGE |  |  | 0
LOW_POWER |  |  | 1
LOW_EFFICIENCY |  |  | 2
CURRENT |  |  | 3
VOLTAGE |  |  | 4
POWER |  |  | 5
PR |  |  | 6
DISCONNECTED |  |  | 7
FUSE_FAULT |  |  | 8
COMBINER_FUSE_FAULT |  |  | 9
COMBINER_CABINET_OPEN |  |  | 10
TEMP |  |  | 11
GROUNDFAULT |  |  | 12
REVERSED_POLARITY |  |  | 13
INCOMPATIBLE |  |  | 14
COMM_ERROR |  |  | 15
INTERNAL_ERROR |  |  | 16
THEFT |  |  | 17
ARC_DETECTED |  |  | 18

## P 501
// 501-Solar Module : A solar module model supporing DC-DC converter (Float)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 501. Uniquely identifies this as a SunSpec Solar Module Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 31 |  | M
// 501 Solar Module Fixed Block (31)
3 | 3 | 1 | R | Stat | Status | enum16 |  |  | Enumerated value. Module Status Code |  | M
4 | 4 | 1 | R | StatVend | Vendor Status | enum16 |  |  | Module Vendor Status Code |  | O
5 | 6 | 2 | R | Evt | Events | bitfield32 |  |  | Bitmask value. Module Event Flags |  | M
7 | 8 | 2 | R | EvtVend | Vendor Module Event Flags | bitfield32 |  |  | Vendor specific flags |  | O
9 | 9 | 1 | RW | Ctl | Control | enum16 |  |  | Module Control |  | O
10 | 11 | 2 | RW | CtlVend | Vendor Control | enum32 |  |  | Vendor Module Control |  | O
12 | 13 | 2 | RW | CtlVal | Control Value | int32 |  |  | Module Control Value |  | O
14 | 15 | 2 | R | Tms | Timestamp | uint32 | Secs |  | Time in seconds since 2000 epoch |  | O
16 | 17 | 2 | R | OutA | Output Current | float32 | A |  | Output Current |  | O
18 | 19 | 2 | R | OutV | Output Voltage | float32 | V |  | Output Voltage |  | O
20 | 21 | 2 | R | OutWh | Output Energy | float32 | Wh |  | Output Energy |  | O
22 | 23 | 2 | R | OutW | Output Power | float32 | W |  | Output Power |  | O
24 | 25 | 2 | R | Tmp | Temp | float32 | C |  | Module Temperature |  | O
26 | 27 | 2 | R | InA | Input Current | float32 | A |  | Input Current |  | O
28 | 29 | 2 | R | InV | Input Voltage | float32 | V |  | Input Voltage |  | O
30 | 31 | 2 | R | InWh | Input Energy | float32 | Wh |  | Input Energy |  | O
32 | 33 | 2 | R | InW | Input Power | float32 | W |  | Input Power |  | O
// Stat enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
OFF |  |  | 1 |  | Off |  | Module is in the OFF state
SLEEPING |  |  | 2 |  | SLEEPING |  | Sleeping (auto-shutdown) or panel is at low/safe output power/voltage
STARTING |  |  | 3 |  | STARTING |  | Starting up or ON but not producting power; panel might have high voltage but is not producing power
MPPT |  |  | 4 |  | MPPT |  | Tracking MPPT power point
THROTTLED |  |  | 5 |  | THROTTLED |  | Forced power reduction / power de-rating
SHUTTING_DOWN |  |  | 6 |  | SHUTTING_DOWN |  | Shutting down
FAULT |  |  | 7 |  | FAULT |  | One or more faults exist
STANDBY |  |  | 8 |  | STANDBY |  | Standby (service or unit) - unlike SLEEPING in this mode the module might be at a high (unsafe) output voltage or power
TEST |  |  | 9 |  | TEST |  | Test mode
OTHER |  |  | 10 |  | OTHER |  | As defined in vendor specific status
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
GROUND_FAULT |  |  | 0 |  | Ground Fault |  | Ground Fault
INPUT_OVER_VOLTAGE |  |  | 1 |  | Over Voltage |  | DC input over-voltage
RESERVED |  |  | 2 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
DC_DISCONNECT |  |  | 3 |  | Disconnect |  | DC disconnect open
RESERVED |  |  | 4 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
RESERVED |  |  | 5 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
MANUAL_SHUTDOWN |  |  | 6 |  | Manual shutdown |  | Manual shutdown
OVER_TEMPERATURE |  |  | 7 |  | Over Temperature |  | Over Temperature
RESERVED |  |  | 8 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
RESERVED |  |  | 9 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
RESERVED |  |  | 10 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
RESERVED |  |  | 11 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
BLOWN_FUSE |  |  | 12 |  | Blown Fuse |  | Input fuse is blown
UNDER_TEMPERATURE |  |  | 13 |  | Under Temperature |  | Under Temperature
MEMORY_LOSS |  |  | 14 |  | Memory Loss |  | Generic Memory or Communication Error
ARC_DETECTION |  |  | 15 |  | Arc Detection |  | Arc Detection
THEFT_DETECTION |  |  | 16 |  | Theft Detection |  | Theft Detection
OUTPUT_OVER_CURRENT |  |  | 17 |  | Over Current |  | Output Over Current
OUTPUT_OVER_VOLTAGE |  |  | 18 |  | Output Over Voltage |  | DC Output Over Voltage
OUTPUT_UNDER_VOLTAGE |  |  | 19 |  | Output Under Voltage |  | DC Output Under Voltage
TEST_FAILED |  |  | 20 |  | Test Failed |  | Last Self Test failed; see vendor event for details

## P 502
// 502-Solar Module : A solar module model supporing DC-DC converter (Integer)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 502. Uniquely identifies this as a SunSpec Solar Module Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 28 |  | M
// 502 Solar Module Fixed Block (28)
3 | 3 | 1 | R | A_SF |  | sunssf |  |  | Current scale factor |  | O
4 | 4 | 1 | R | V_SF |  | sunssf |  |  | Voltage scale factor |  | O
5 | 5 | 1 | R | W_SF |  | sunssf |  |  | Power scale factor |  | O
6 | 6 | 1 | R | Wh_SF |  | sunssf |  |  | Energy scale factor |  | O
7 | 7 | 1 | R | Stat | Status | enum16 |  |  | Enumerated value. Module Status Code |  | M
8 | 8 | 1 | R | StatVend | Vendor Status | enum16 |  |  | Module Vendor Status Code |  | O
9 | 10 | 2 | R | Evt | Events | bitfield32 |  |  | Bitmask value. Module Event Flags |  | M
11 | 12 | 2 | R | EvtVend | Vendor Module Event Flags | bitfield32 |  |  | Vendor specific flags |  | O
13 | 13 | 1 | RW | Ctl | Control | enum16 |  |  | Module Control |  | O
14 | 15 | 2 | RW | CtlVend | Vendor Control | enum32 |  |  | Vendor Module Control |  | O
16 | 17 | 2 | RW | CtlVal | Control Value | int32 |  |  | Module Control Value |  | O
18 | 19 | 2 | R | Tms | Timestamp | uint32 | Secs |  | Time in seconds since 2000 epoch |  | O
20 | 20 | 1 | R | OutA | Output Current | int16 | A | A_SF | Output Current |  | O
21 | 21 | 1 | R | OutV | Output Voltage | int16 | V | V_SF | Output Voltage |  | O
22 | 23 | 2 | R | OutWh | Output Energy | acc32 | Wh | Wh_SF | Output Energy |  | O
24 | 24 | 1 | R | OutPw |  | int16 | W | W_SF |  |  | O
25 | 25 | 1 | R | Tmp | Temp | int16 | C |  | Module Temperature |  | O
26 | 26 | 1 | R | InA | Input Current | int16 | A | A_SF | Input Current |  | O
27 | 27 | 1 | R | InV | Input Voltage | int16 | V | V_SF | Input Voltage |  | O
28 | 29 | 2 | R | InWh | Input Energy | acc32 | Wh | Wh_SF | Input Energy |  | O
30 | 30 | 1 | R | InW | Input Power | int16 | W | W_SF | Input Power |  | O
// Stat enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
OFF |  |  | 1 |  | Off |  | Module is in the OFF state
SLEEPING |  |  | 2 |  | SLEEPING |  | Sleeping (auto-shutdown) or panel is at low/safe output power/voltage
STARTING |  |  | 3 |  | STARTING |  | Starting up or ON but not producting power; panel might have high voltage but is not producing power
MPPT |  |  | 4 |  | MPPT |  | Tracking MPPT power point
THROTTLED |  |  | 5 |  | THROTTLED |  | Forced power reduction / power de-rating
SHUTTING_DOWN |  |  | 6 |  | SHUTTING_DOWN |  | Shutting down
FAULT |  |  | 7 |  | FAULT |  | One or more faults exist
STANDBY |  |  | 8 |  | STANDBY |  | Standby (service or unit) - unlike SLEEPING in this mode the module might be at a high (unsafe) output voltage or power
TEST |  |  | 9 |  | TEST |  | Test mode
OTHER |  |  | 10 |  | OTHER |  | As defined in vendor specific status
// Evt bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
GROUND_FAULT |  |  | 0 |  | Ground Fault |  | Ground Fault
INPUT_OVER_VOLTAGE |  |  | 1 |  | Over Voltage |  | DC input over-voltage
RESERVED |  |  | 2 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
DC_DISCONNECT |  |  | 3 |  | Disconnect |  | DC disconnect open
RESERVED |  |  | 4 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
RESERVED |  |  | 5 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
MANUAL_SHUTDOWN |  |  | 6 |  | Manual shutdown |  | Manual shutdown
OVER_TEMPERATURE |  |  | 7 |  | Over Temperature |  | Over Temperature
RESERVED |  |  | 8 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
RESERVED |  |  | 9 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
RESERVED |  |  | 10 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
RESERVED |  |  | 11 |  | Reserved |  | Reserved |  | Reserved for u-inverter compatibility
BLOWN_FUSE |  |  | 12 |  | Blown Fuse |  | Input fuse is blown
UNDER_TEMPERATURE |  |  | 13 |  | Under Temperature |  | Under Temperature
MEMORY_LOSS |  |  | 14 |  | Memory Loss |  | Generic Memory or Communication Error
ARC_DETECTION |  |  | 15 |  | Arc Detection |  | Arc Detection
THEFT_DETECTION |  |  | 16 |  | Theft Detection |  | Theft Detection
OUTPUT_OVER_CURRENT |  |  | 17 |  | Over Current |  | Output Over Current
OUTPUT_OVER_VOLTAGE |  |  | 18 |  | Output Over Voltage |  | DC Output Over Voltage
OUTPUT_UNDER_VOLTAGE |  |  | 19 |  | Output Under Voltage |  | DC Output Under Voltage
TEST_FAILED |  |  | 20 |  | Test Failed |  | Last Self Test failed; see vendor event for details

## T 601
// 601-Tracker Controller DRAFT 2 : Monitors and controls multiple trackers (Trackers may include GPS model 305 for location information)
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 601. Uniquely identifies this as a SunSpec Tracker Controller DRAFT 2 Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 26+N*22 |  | M
// 601 Tracker Controller DRAFT 2 Fixed Block (26)
3 | 10 | 8 | R | Nam | Controller | string |  |  | Descriptive name for this control unit |  | O
11 | 11 | 1 | R | Typ | Type | enum16 |  |  | Type of tracker |  | M
12 | 16 | 5 | R | DtLoc | Date | string | YYYYMMDD |  | Local date in YYYYMMDD format |  | O
17 | 19 | 3 | R | TmLoc | Time | string | hhmmss |  | 24 hour local time stamp to second |  | O
20 | 20 | 1 | R | Day | Day | uint16 |  |  | Number of the day in the year (1-366) |  | O
21 | 22 | 2 | RW | GlblElCtl | Manual Elevation | int32 | Degrees | Dgr_SF | Global manual override target position of elevation in degreees from horizontal. Unimplemented for single axis azimuth tracker type |  | O
23 | 24 | 2 | RW | GlblAzCtl | Manual Azimuth | int32 | Degrees | Dgr_SF | Global manual override target position of azimuth in degrees from true north towards east. Unimplemented for single axis azimuth tracker type |  | O
25 | 25 | 1 | RW | GlblCtl | Mode | enum16 |  |  | Global Control register operates on all trackers. Normal operation is automatic. Operator can override the position by setting the ElCtl, AzCtl and enabling Manual operation. Entering calibration mode will revert to automatic operation after calibration is complete. |  | O
26 | 26 | 1 | R | GlblAlm | Alarm | bitfield16 |  |  | Global tracker alarm conditions |  | O
27 | 27 | 1 | R | Dgr_SF | SF | sunssf |  |  | Scale Factor for targets and position measurements in degrees |  | M
28 | 28 | 1 | R | N | Trackers | uint16 |  |  | Number of trackers being controlled. Size of repeating block. |  | M
// 601 Tracker Controller DRAFT 2 Repeating Block (22)
29 | 36 | 8 | R | Id | Tracker | string |  |  | Descriptive name for this tracker unit |  | O
37 | 38 | 2 | R | ElTrgt | Target Elevation | int32 | Degrees | Dgr_SF | Auto target elevation in degrees from horizontal. Unimplemented for single axis azimuth tracker type | Conformant implementations shall implement El or Az | O
39 | 40 | 2 | R | AzTrgt | Target Azimuth | int32 | Degrees | SF | Auto target azimuth in degrees from true north towards east. Unimplemented for single axis horizontal tracker type | Conformant implementations shall implement El or Az | O
41 | 42 | 2 | R | ElPos | Elevation | int32 | Degrees | Dgr_SF | Actual elevation position in degrees from horizontal. Unimplemented for single axis azimuth tracker type | Conformant implementations shall implement El or Az | O
43 | 44 | 2 | R | AzPos | Azimuth | int32 | Degrees | Dgr_SF | Actual azimuth position in degrees from true north towards east. Unimplemented for single axis horizontal tracker type | Conformant implementations shall implement El or Az | O
45 | 46 | 2 | RW | ElCtl | Manual Elevation | int32 | Degrees | Dgr_SF | Manual override target position of elevation in degreees from horizontal. Unimplemented for single axis azimuth tracker type |  | O
47 | 48 | 2 | RW | AzCtl | Manual Azimuth | int32 | Degrees | Dgr_SF | Manual override target position of azimuth in degrees from true north towards east. Unimplemented for single axis azimuth tracker type |  | O
49 | 49 | 1 | RW | Ctl | Mode | enum16 |  |  | Control register. Normal operation is automatic. Operator can override the position by setting the ElCtl, AzCtl and enabling Manual operation. Entering calibration mode will revert to automatic operation after calibration is complete. |  | O
50 | 50 | 1 | R | Alm | Alarm | bitfield16 |  |  | Tracker alarm conditions |  | O
// Typ enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Unknown |  |  | 0 |  | Unknown |  | Not Set
Fixed |  |  | 1 |  | Fixed |  | Documented orientation information
Horizontal |  |  | 2 |  | Horizontal |  | Single Axis Horizontal
Tilted |  |  | 3 |  | Tilted |  | Single Axis Tilted Horizontal
Azimuth |  |  | 4 |  | Azimuth |  | Single Axis Azimuth
Dual |  |  | 5 |  | Dual |  | Dual Axis
Other |  |  | 99 |  | Other |  | Other type
// Ctl enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Automatic |  |  | 0 |  | Auto |  | Follow programmed path
Manual |  |  | 1 |  | Manual |  | Go to a fixed position
Calibrate |  |  | 2 |  | Calibrate |  | Execute test mode
// GlblCtl enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Automatic |  |  | 0 |  | Auto |  | Follow programmed path
Manual |  |  | 1 |  | Manual |  | Go to a fixed position
Calibrate |  |  | 2 |  | Calibrate |  | Execute test mode
// Alm bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
SetPoint |  |  | 0 |  | SetPoint |  | Tracker NOT at SetPoint
ObsEl |  |  | 1 |  | ObsEl |  | Tracker ELEVATION motor is obstructed
ObsAz |  |  | 2 |  | ObsAz |  | Tracker AZIMUTH motor is obstructed
// GlblAlm bit identifiers
ID |  |  | Bit |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
SetPoint |  |  | 0 |  | SetPoint |  | One or more trackers are NOT at SetPoint
ObsEl |  |  | 1 |  | ObsEl |  | One or more trackers ELEVATION motor is obstructed
ObsAz |  |  | 2 |  | ObsAz |  | One or more trackers AZIMUTH motor is obstructed

## V 64001
// 64001-Veris Status and Configuration : ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 64001. Uniquely identifies this as a SunSpec Veris Status and Configuration Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 71 |  | M
// 64001 Veris Status and Configuration Fixed Block (71)
3 | 3 | 1 | RW | Cmd | Command Code | enum16 |  |  |  |  | O
4 | 4 | 1 | R | HWRev | Hardware Revision | uint16 |  |  |  |  | O
5 | 5 | 1 | R | RSFWRev | RS FW Revision | uint16 |  |  |  |  | O
6 | 6 | 1 | R | OSFWRev | OS FW Revision | uint16 |  |  |  |  | O
7 | 8 | 2 | R | ProdRev | Product Revision | string |  |  |  |  | O
9 | 9 | 1 | R | Boots | Boot Count | uint16 |  |  |  |  | O
10 | 10 | 1 | R | Switch | DIP Switches | bitfield16 |  |  |  |  | O
11 | 11 | 1 | R | Sensors | Num Detected Sensors | uint16 |  |  |  |  | O
12 | 12 | 1 | R | Talking | Num Communicating Sensors | uint16 |  |  |  |  | O
13 | 13 | 1 | R | Status | System Status | bitfield16 |  |  |  |  | O
14 | 14 | 1 | R | Config | System Configuration | bitfield16 |  |  |  |  | O
15 | 15 | 1 | R | LEDblink | LED Blink Threshold | uint16 | Pct |  |  |  | O
16 | 16 | 1 | R | LEDon | LED On Threshold | uint16 | Pct |  |  |  | O
17 | 17 | 1 | R | Reserved |  | uint16 |  |  |  |  | O
18 | 33 | 16 | R | Loc | Location String | string |  |  |  |  | O
34 | 34 | 1 | R | S1ID | Sensor 1 Unit ID | enum16 |  |  |  |  | O
35 | 35 | 1 | R | S1Addr | Sensor 1 Address | uint16 |  |  |  |  | O
36 | 36 | 1 | R | S1OSVer | Sensor 1 OS Version | uint16 |  |  |  |  | O
37 | 38 | 2 | R | S1Ver | Sensor 1 Product Version | string |  |  |  |  | O
39 | 43 | 5 | R | S1Serial | Sensor 1 Serial Num | string |  |  |  |  | O
44 | 44 | 1 | R | S2ID | Sensor 2 Unit ID | enum16 |  |  |  |  | O
45 | 45 | 1 | R | S2Addr | Sensor 2 Address | uint16 |  |  |  |  | O
46 | 46 | 1 | R | S2OSVer | Sensor 2 OS Version | uint16 |  |  |  |  | O
47 | 48 | 2 | R | S2Ver | Sensor 2 Product Version | string |  |  |  |  | O
49 | 53 | 5 | R | S2Serial | Sensor 2 Serial Num | string |  |  |  |  | O
54 | 54 | 1 | R | S3ID | Sensor 3 Unit ID | enum16 |  |  |  |  | O
55 | 55 | 1 | R | S3Addr | Sensor 3 Address | uint16 |  |  |  |  | O
56 | 56 | 1 | R | S3OSVer | Sensor 3 OS Version | uint16 |  |  |  |  | O
57 | 58 | 2 | R | S3Ver | Sensor 3 Product Version | string |  |  |  |  | O
59 | 63 | 5 | R | S3Serial | Sensor 3 Serial Num | string |  |  |  |  | O
64 | 64 | 1 | R | S4ID | Sensor 4 Unit ID | enum16 |  |  |  |  | O
65 | 65 | 1 | R | S4Addr | Sensor 4 Address | uint16 |  |  |  |  | O
66 | 66 | 1 | R | S4OSVer | Sensor 4 OS Version | uint16 |  |  |  |  | O
67 | 68 | 2 | R | S4Ver | Sensor 4 Product Version | string |  |  |  |  | O
69 | 73 | 5 | R | S4Serial | Sensor 4 Serial Num | string |  |  |  |  | O

## V 64020
// 64020-Mersen GreenString : ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 64020. Uniquely identifies this as a SunSpec Mersen GreenString Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Variable # of 16 bit registers to follow : 30+N*16 |  | M
// 64020 Mersen GreenString Fixed Block (30)
3 | 3 | 1 | R | Aux0Tmp | Aux 0 temperature | int16 | C |  |  |  | O
4 | 4 | 1 | R | Aux1Tmp | Aux 1 temperature | int16 | C |  |  |  | O
5 | 5 | 1 | R | Aux2Tmp | Aux 2 temperature | int16 | C |  |  |  | O
6 | 6 | 1 | R | Aux3Tmp | Aux 3 temperature | int16 | C |  |  |  | O
7 | 7 | 1 | R | Aux4Tmp | Aux 4 temperature | int16 | C |  |  |  | O
8 | 8 | 1 | R | MainTmp | Main Temperature | int16 | C |  |  |  | M
9 | 9 | 1 | R | ProbeTmp | Probe Temperature | int16 | C |  |  |  | M
10 | 10 | 1 | R | SensorV_SF | Voltage scale factor for the sensors | sunssf |  |  |  |  | M
11 | 11 | 1 | R | SensorA_SF | Current scale factor for the sensors | sunssf |  |  |  |  | M
12 | 12 | 1 | R | SensorHz_SF | Frequency scale factor for the sensors | sunssf |  |  |  |  | M
13 | 13 | 1 | R | Sensor1Voltage | Sensor1 Voltage | int16 | V | SensorV_SF | scale of 0-10V |  | O
14 | 14 | 1 | R | Sensor2Voltage | Sensor2 Voltage | int16 | V | SensorV_SF | scale of 0-10V |  | O
15 | 15 | 1 | R | Sensor3Voltage | Sensor3 Voltage | int16 | V | SensorV_SF | scale of 0-10V |  | O
16 | 16 | 1 | R | Sensor4Voltage | Sensor4 Voltage | int16 | V | SensorV_SF | scale of 0-10V |  | O
17 | 17 | 1 | R | Sensor5Voltage | Sensor5 Voltage | int16 | V | SensorV_SF | scale of 0-10V |  | O
18 | 18 | 1 | R | Sensor6Voltage | Sensor6 Voltage | int16 | V | SensorV_SF | scale of 0-10V |  | O
19 | 19 | 1 | R | Sensor7Voltage | Sensor7 Voltage | int16 | V | SensorV_SF | scale of 0-10V |  | O
20 | 20 | 1 | R | Sensor1Current | Sensor1 Current | int16 | A | SensorA_SF | scale of 4-20mA |  | O
21 | 21 | 1 | R | Sensor2Current | Sensor2 Current | int16 | A | SensorA_SF | in 4-20mA or 4-20mA |  | O
22 | 22 | 1 | R | Sensor3Current | Sensor3 Current | int16 | A | SensorA_SF | in 4-20mA or 4-20mA |  | O
23 | 23 | 1 | R | Sensor4Current | Sensor4 Current | int16 | A | SensorA_SF | in 4-20mA or 4-20mA |  | O
24 | 24 | 1 | R | Sensor5Current | Sensor5 Current | int16 | A | SensorA_SF | in 4-20mA or 4-20mA |  | O
25 | 25 | 1 | R | Sensor6Current | Sensor6 Current | int16 | A | SensorA_SF | in 4-20mA or 4-20mA |  | O
26 | 26 | 1 | R | Sensor7Current | Sensor7 Current | int16 | A | SensorA_SF | in 4-20mA or 4-20mA |  | O
27 | 27 | 1 | R | Sensor8 | Sensor8 frequency | uint16 | Hz | SensorHz_SF | frequency in Hz |  | O
28 | 28 | 1 | R | Relay1 | Relay 1 state | uint16 |  |  |  |  | O
29 | 29 | 1 | R | Relay2 | Relay 2 state | uint16 |  |  |  |  | O
30 | 30 | 1 | R | Relay3 | Relay 3 state | uint16 |  |  |  |  | O
31 | 31 | 1 | R | ResetAccumulators | Reset the accumulators | uint16 |  |  | always 0 in reading, used the code 0xC0DA during the writting for resetting them |  | O
32 | 32 | 1 | R | Reset | Reset the system | uint16 |  |  | always 0 in reading, used the code 0xC0DA during the writting for resetting the system |  | O
// 64020 Mersen GreenString Repeating Block (16)
33 | 41 | 9 | R | SerialNumber | Serial number | string |  |  | strings of 16 caracters |  | M
42 | 47 | 6 | R | Firmware | Firmware version | string |  |  | string of 11 caracters |  | M
48 | 48 | 1 | R | Hardware | Hardware version | uint16 |  |  |  |  | M

## V 64101
// 64101-Eltek Inverter Extension : ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 64101. Uniquely identifies this as a SunSpec Eltek Inverter Extension Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 7 |  | M
// 64101 Eltek Inverter Extension Fixed Block (7)
3 | 3 | 1 | R | Eltek_Country_Code |  | uint16 |  |  |  |  | O
4 | 4 | 1 | R | Eltek_Feeding_Phase |  | uint16 |  |  |  |  | O
5 | 5 | 1 | R | Eltek_APD_Method |  | uint16 |  |  |  |  | O
6 | 6 | 1 | R | Eltek_APD_Power_Ref |  | uint16 |  |  |  |  | O
7 | 7 | 1 | R | Eltek_RPS_Method |  | uint16 |  |  |  |  | O
8 | 8 | 1 | R | Eltek_RPS_Q_Ref |  | uint16 |  |  |  |  | O
9 | 9 | 1 | R | Eltek_RPS_CosPhi_Ref |  | int16 |  |  |  |  | O

## V 64110
// 64110-OutBack AXS device : ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 64110. Uniquely identifies this as a SunSpec OutBack AXS device Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 282 |  | M
// 64110 OutBack AXS device Fixed Block (282)
3 | 3 | 1 | R | MajorFWRev | AXS Major Firmware Number | uint16 |  |  |  |  | M
4 | 4 | 1 | R | MidFWRev | AXS Mid Firmware Number | uint16 |  |  |  |  | M
5 | 5 | 1 | R | MinorFWRev | AXS Minor Firmware Number | uint16 |  |  |  |  | M
6 | 6 | 1 | R | EncrypKey | Encryption Key | uint16 |  |  |  |  | M
7 | 13 | 7 | R | MAC_Address | MAC Address | string |  |  |  |  | M
14 | 21 | 8 | R | WritePassword | Write Password | string |  |  |  |  | M
22 | 22 | 1 | R | EnableDHCP | Enable DHCP | enum16 |  |  |  |  | M
23 | 24 | 2 | R | TCPIP_address | TCPIP Address | ipaddr |  |  |  |  | M
25 | 26 | 2 | R | Gateway_address | TCPIP Gateway | ipaddr |  |  |  |  | M
27 | 28 | 2 | R | TCPIP_Netmask | TCPIP Netmask | ipaddr |  |  |  |  | M
29 | 30 | 2 | R | DNS1_address | TCPIP DNS1 | ipaddr |  |  |  |  | M
31 | 32 | 2 | R | DNS2_address | TCPIP DNS2 | ipaddr |  |  |  |  | M
33 | 33 | 1 | R | Modbus_port | ModBus Port | uint16 |  |  |  |  | M
34 | 53 | 20 | R | SMTP_server_nm | SMTP Server Name | string |  |  |  |  | M
54 | 69 | 16 | R | SMTP_account_nm | SMTP Account Name | string |  |  |  |  | M
70 | 70 | 1 | R | SMTP_enable_SSL | Enable SMTP SSL | enum16 |  |  |  |  | M
71 | 78 | 8 | R | SMTP_password | SMTP Password | string |  |  |  |  | M
79 | 98 | 20 | R | SMTP_user_nm | SMTP User Name | string |  |  |  |  | M
99 | 99 | 1 | R | Stat_email_int | Status Email Interval | uint16 |  |  |  |  | M
100 | 100 | 1 | R | Stat_start_HR | Status Email Start Hour | uint16 |  |  |  |  | M
101 | 125 | 25 | R | Stat_email_sub | Status Email Subject | string |  |  |  |  | M
126 | 145 | 20 | R | Stat_email_addr1 | Status Email to Address 1 | string |  |  |  |  | M
146 | 165 | 20 | R | Stat_email_addr2 | Status Email to Address 2 | string |  |  |  |  | M
166 | 166 | 1 | R | Alarm_email_en | Enable Alarm Email | enum16 |  |  |  |  | M
167 | 191 | 25 | R | Alarm_email_sub | Alarm Email Subject | string |  |  |  |  | M
192 | 211 | 20 | R | Alarm_email_addr1 | Alarm Email to Address 1 | string |  |  |  |  | M
212 | 231 | 20 | R | Alarm_email_addr2 | Alarm Email to Address 2 | string |  |  |  |  | M
232 | 239 | 8 | R | FTP_password | FTP Password | string |  |  |  |  | M
240 | 247 | 8 | R | TELNET_password | Telnet Password | string |  |  |  |  | M
248 | 248 | 1 | R | Log_write_int | SD-Card Datalog Write Interval | uint16 | Tms |  |  |  | M
249 | 249 | 1 | R | Log_retain | SD-Card Datalog Retain | uint16 | Tmd |  |  |  | M
250 | 250 | 1 | R | Log_mode | SD-Card Datalog Mode | enum16 |  |  |  |  | M
251 | 270 | 20 | R | NTP_server_nm | NTP Timer Server Name | string |  |  |  |  | M
271 | 271 | 1 | R | NTP_enable | Enable Network Time | enum16 |  |  |  |  | M
272 | 272 | 1 | R | TimeZone | Time Zone | int16 | Tmh |  |  |  | M
273 | 273 | 1 | R | Date_year | Year | uint16 |  |  |  |  | M
274 | 274 | 1 | R | Date_month | Month | uint16 |  |  |  |  | M
275 | 275 | 1 | R | Date_Day | Day | uint16 |  |  |  |  | M
276 | 276 | 1 | R | Time_hour | Hour | uint16 |  |  |  |  | M
277 | 277 | 1 | R | Time_minute | Minute | uint16 |  |  |  |  | M
278 | 278 | 1 | R | Time_second | Second | uint16 |  |  |  |  | M
279 | 279 | 1 | R | Battery_temp | Battery Temperature | int16 | C | Temp_SF |  |  | M
280 | 280 | 1 | R | Ambient_temp | Ambient Temperature | int16 | C | Temp_SF |  |  | M
281 | 281 | 1 | R | Temp_SF |  | sunssf |  |  |  |  | M
282 | 282 | 1 | R | AXS_Error | AXS Error | bitfield16 |  |  |  |  | M
283 | 283 | 1 | R | AXS_Status | AXS Status | bitfield16 |  |  |  |  | M
284 | 284 | 1 | R | AXS_Spare | Spare | uint16 |  |  |  |  | M
// SMTP_enable_SSL enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ASX_DISABLED |  |  | 0 |  | Disabled
ASX_ENABLED |  |  | 1 |  | Enabled
// Alarm_email_en enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ASX_DISABLED |  |  | 0 |  | Disabled
ASX_ENABLED |  |  | 1 |  | Enabled
// Log_mode enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
LOG_DISABLED |  |  | 0 |  | Disabled
LOG_EXCEL |  |  | 1 |  | Excel
LOG_COMPACT |  |  | 2 |  | Compact
// NTP_enable enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
ASX_DISABLED |  |  | 0 |  | Disabled
ASX_ENABLED |  |  | 1 |  | Enabled

## V 64111
// 64111-Basic Charge Controller : ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 64111. Uniquely identifies this as a SunSpec Basic Charge Controller Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 23 |  | M
// 64111 Basic Charge Controller Fixed Block (23)
3 | 3 | 1 | R | Port | Port Number | uint16 |  |  |  |  | M
4 | 4 | 1 | R | V_SF |  | sunssf |  |  |  |  | M
5 | 5 | 1 | R | A_SF |  | sunssf |  |  |  |  | M
6 | 6 | 1 | R | P_SF |  | sunssf |  |  |  |  | M
7 | 7 | 1 | R | AH_SF |  | sunssf |  |  |  |  | M
8 | 8 | 1 | R | KWH_SF |  | sunssf |  |  |  |  | M
9 | 9 | 1 | R | BattV | Battery Voltage | uint16 | V | V_SF |  |  | M
10 | 10 | 1 | R | ArrayV | Array Voltage | uint16 | V | V_SF |  |  | M
11 | 11 | 1 | R | OutputA | Output Current | uint16 | A | A_SF |  |  | M
12 | 12 | 1 | R | InputA | Array Current | uint16 | A | P_SF |  |  | M
13 | 13 | 1 | R | ChargerSt | Operating State | enum16 |  |  |  |  | M
14 | 14 | 1 | R | OutputW | Output Wattage | uint16 | W | P_SF |  |  | M
15 | 15 | 1 | R | TodayMinBatV | Todays Minimum Battery Voltage | uint16 | V | V_SF |  |  | M
16 | 16 | 1 | R | TodayMaxBatV | Todays Maximum Battery Voltage | uint16 | V | V_SF |  |  | M
17 | 17 | 1 | R | VOCV | VOC | uint16 | V | V_SF |  |  | M
18 | 18 | 1 | R | TodayMaxVOC | Todays Maximum VOC | uint16 | V | V_SF |  |  | M
19 | 19 | 1 | R | TodaykWhOutput | Todays kWh | uint16 | kWh | KWH_SF |  |  | M
20 | 20 | 1 | R | TodayAHOutput | Todays AH | uint16 | AH | AH_SF |  |  | M
21 | 21 | 1 | R | LifeTimeKWHOut | Lifetime kWh | uint16 | kWh | P_SF |  |  | M
22 | 22 | 1 | R | LifeTimeAHOut | Lifetime kAH | uint16 | kAH | KWH_SF |  |  | M
23 | 23 | 1 | R | LifeTimeMaxOut | Lifetime Maximum Output Wattage | uint16 | W | P_SF |  |  | M
24 | 24 | 1 | R | LifeTimeMaxBatt | Lifetime Maximum Battery Voltage | uint16 | V | V_SF |  |  | M
25 | 25 | 1 | R | LifeTimeMaxVOC | Lifetime Maximum VOC Voltage | uint16 | V | V_SF |  |  | M
// ChargerSt enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Off |  |  | 0 |  | Off
Float |  |  | 1 |  | Float Charging
Bulk |  |  | 2 |  | Bulk Charging
Absorb |  |  | 3 |  | Absorb Charging
EQ |  |  | 4 |  | Equilize Charging

## V 64112
// 64112-OutBack FM Charge Controller : ()
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 64112. Uniquely identifies this as a SunSpec OutBack FM Charge Controller Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16 bit registers to follow : 64 |  | M
// 64112 OutBack FM Charge Controller Fixed Block (64)
3 | 3 | 1 | R | Port | Port Number | uint16 |  |  |  |  | M
4 | 4 | 1 | R | V_SF |  | sunssf |  |  |  |  | M
5 | 5 | 1 | R | C_SF |  | sunssf |  |  |  |  | M
6 | 6 | 1 | R | H_SF |  | sunssf |  |  |  |  | M
7 | 7 | 1 | R | P_SF |  | sunssf |  |  |  |  | M
8 | 8 | 1 | R | AH_SF |  | sunssf |  |  |  |  | M
9 | 9 | 1 | R | KWH_SF |  | sunssf |  |  |  |  | M
10 | 10 | 1 | R | CC_Config_fault | Faults | bitfield16 |  |  |  |  | M
11 | 11 | 1 | R | CC_Config_absorb_V | Absorb | uint16 | V | V_SF |  |  | M
12 | 12 | 1 | R | CC_Config_absorb_Hr | Absorb Time | uint16 | Tmh | H_SF |  |  | M
13 | 13 | 1 | R | CC_Config_absorb_End_A | Absorb End | uint16 | A | V_SF |  |  | M
14 | 14 | 1 | R | CC_Config_rebulk_V | Rebulk | uint16 | V | V_SF |  |  | M
15 | 15 | 1 | R | CC_Config_float_V | Float | uint16 | V | V_SF |  |  | M
16 | 16 | 1 | R | CC_Config_max_Chg_A | Maximum Charge | uint16 | A | V_SF |  |  | M
17 | 17 | 1 | R | CC_Config_equalize_V | Equalize | uint16 | V | V_SF |  |  | M
18 | 18 | 1 | R | CC_Config_equalize_Hr | Equalize Time | uint16 | Tmh |  |  |  | M
19 | 19 | 1 | R | CC_Config_auto_equalize | Auto Equalize Interval | uint16 | Tmd |  |  |  | M
20 | 20 | 1 | R | CC_Config_MPPT_mode | MPPT mode | enum16 |  |  |  |  | M
21 | 21 | 1 | R | CC_Config_sweep_width | Sweep Width | enum16 |  |  |  |  | M
22 | 22 | 1 | R | CC_Config_sweep_max | Sweep Maximum | enum16 |  |  |  |  | M
23 | 23 | 1 | R | CC_Config_U_Pick_Duty_cyc | U-Pick PWM Duty Cycle | uint16 | Pct | V_SF |  |  | M
24 | 24 | 1 | R | CC_Config_grid_tie | Grid Tie Mode | enum16 |  |  |  |  | M
25 | 25 | 1 | R | CC_Config_temp_comp | Temp Comp Mode | enum16 |  |  |  |  | M
26 | 26 | 1 | R | CC_Config_temp_comp_llimt | Temp Comp Lower Limit | uint16 | V | V_SF |  |  | M
27 | 27 | 1 | R | CC_Config_temp_comp_hlimt | Temp Comp Upper Limit | uint16 | V | V_SF |  |  | M
28 | 28 | 1 | R | CC_Config_auto_restart | Auto Restart Mode | enum16 |  |  |  |  | M
29 | 29 | 1 | R | CC_Config_wakeup_VOC | Wakeup VOC Change | uint16 | V | V_SF |  |  | M
30 | 30 | 1 | R | CC_Config_snooze_mode_A | Snooze Mode | uint16 | A | V_SF |  |  | M
31 | 31 | 1 | R | CC_Config_wakeup_interval | Wakeup Interval | uint16 | Tms |  |  |  | M
32 | 32 | 1 | R | CC_Config_AUX_mode | AUX Output Mode | enum16 |  |  |  |  | M
33 | 33 | 1 | R | CC_Config_AUX_control | AUX Output Control | enum16 |  |  |  |  | M
34 | 34 | 1 | R | CC_Config_AUX_state | AUX Output State | enum16 |  |  |  |  | M
35 | 35 | 1 | R | CC_Config_AUX_polarity | AUX Output Polarity | enum16 |  |  |  |  | M
36 | 36 | 1 | R | CC_Config_AUX_L_Batt_disc | AUX Low Battery Disconnect | uint16 | V | V_SF |  |  | M
37 | 37 | 1 | R | CC_Config_AUX_L_Batt_rcon | AUX Low Battery Reconnect | uint16 | V | V_SF |  |  | M
38 | 38 | 1 | R | CC_Config_AUX_L_Batt_dly | AUX Low Battery Disconnect Delay | uint16 | Tms |  |  |  | M
39 | 39 | 1 | R | CC_Config_AUX_Vent_fan_V | AUX Vent Fan | uint16 | V | V_SF |  |  | M
40 | 40 | 1 | R | CC_Config_AUX_PV_triggerV | AUX PV Trigger | uint16 | V | V_SF |  |  | M
41 | 41 | 1 | R | CC_Config_AUX_PV_trg_h_tm | AUX PV Trigger Hold Time | uint16 | Tms |  |  |  | M
42 | 42 | 1 | R | CC_Config_AUX_Nlite_ThrsV | AUX Night Light Threshold | uint16 | V | V_SF |  |  | M
43 | 43 | 1 | R | CC_Config_AUX_Nlite_On_tm | AUX Night Light On Time | uint16 | Tmh | H_SF |  |  | M
44 | 44 | 1 | R | CC_Config_AUX_Nlite_On_hist | AUX Night Light On Hysterisis | uint16 | Tms |  |  |  | M
45 | 45 | 1 | R | CC_Config_AUX_Nlite_Off_hist | AUX Night Light Off Hysterisis | uint16 | Tms |  |  |  | M
46 | 46 | 1 | R | CC_Config_AUX_Error_batt_V | AUX Error Output Low Battery | uint16 | V | V_SF |  |  | M
47 | 47 | 1 | R | CC_Config_AUX_Divert_h_time | AUX Divert Hold Time | uint16 | Tms | V_SF |  |  | M
48 | 48 | 1 | R | CC_Config_AUX_Divert_dly_time | AUX Divert Delay Time | uint16 | Tms |  |  |  | M
49 | 49 | 1 | R | CC_Config_AUX_Divert_Rel_V | AUX Divert Relative | uint16 | V | V_SF |  |  | M
50 | 50 | 1 | R | CC_Config_AUX_Divert_Hyst_V | AUX Divert Hysterisis | uint16 | V | V_SF |  |  | M
51 | 51 | 1 | R | CC_Config_MajorFWRev | FM CC Major Firmware Number | uint16 |  |  |  |  | M
52 | 52 | 1 | R | CC_Config_MidFWRev | FM CC Mid Firmware Number | uint16 |  |  |  |  | M
53 | 53 | 1 | R | CC_Config_MinorFWRev | FM CC Minor Firmware Number | uint16 |  |  |  |  | M
54 | 54 | 1 | R | CC_Config_DataLog_Day_offset | Set Data Log Day Offset | uint16 | Tmd |  |  |  | M
55 | 55 | 1 | R | CC_Config_DataLog_Cur_Day_off | Current Data Log Day Offset | uint16 | Tmd |  |  |  | M
56 | 56 | 1 | R | CC_Config_DataLog_Daily_AH | Data Log Daily | uint16 | Ah |  |  |  | M
57 | 57 | 1 | R | CC_Config_DataLog_Daily_KWH | Data Log Daily | uint16 | kWh | KWH_SF |  |  | M
58 | 58 | 1 | R | CC_Config_DataLog_Max_Out_A | Data Log Daily Maximum Output | uint16 | A | V_SF |  |  | M
59 | 59 | 1 | R | CC_Config_DataLog_Max_Out_W | Data Log Daily Maximum Output | uint16 | W | V_SF |  |  | M
60 | 60 | 1 | R | CC_Config_DataLog_Absorb_T | Data Log Daily Absorb Time | uint16 | Tms |  |  |  | M
61 | 61 | 1 | R | CC_Config_DataLog_Float_T | Data Log Daily Float Time | uint16 | Tms |  |  |  | M
62 | 62 | 1 | R | CC_Config_DataLog_Min_Batt_V | Data Log Daily Minimum Battery | uint16 | V | V_SF |  |  | M
63 | 63 | 1 | R | CC_Config_DataLog_Max_Batt_V | Data Log Daily Maximum Battery | uint16 | V | V_SF |  |  | M
64 | 64 | 1 | R | CC_Config_DataLog_Max_Input_V | Data Log Daily Maximum Input | uint16 | V | V_SF |  |  | M
65 | 65 | 1 | R | CC_Config_DataLog_Clear | Data Log Clear | uint16 |  |  |  |  | M
66 | 66 | 1 | R | CC_Config_DataLog_Clr_Comp | Data Log Clear Complement | uint16 |  |  |  |  | M
// CC_Config_MPPT_mode enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Auto |  |  | 0 |  | Auto
U_Pick |  |  | 1 |  | U-Pick
Wind |  |  | 2 |  | Wind
// CC_Config_sweep_width enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Half |  |  | 0 |  | Half
Full |  |  | 1 |  | Full
// CC_Config_sweep_max enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Eighty_Percent |  |  | 0 |  | 80 %
Eighty_Five_Percent |  |  | 1 |  | 85 %
Ninty_Percent |  |  | 2 |  | 90 %
Ninty_Nine_Percent |  |  | 3 |  | 99 %
// CC_Config_grid_tie enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Disabled |  |  | 0 |  | Grid Tie Mode Disabled
Enabled |  |  | 1 |  | Grid Tie Mode Enabled
// CC_Config_temp_comp enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Wide |  |  | 0 |  | Wide
Limited |  |  | 1 |  | Limited
// CC_Config_auto_restart enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Off |  |  | 0 |  | Off
Every_90_Minutes |  |  | 1 |  | Every 90 Minutes
Every_90_Minutes_if_Absorb_or_Float |  |  | 2 |  | Every 90 Minutes if Absorb or Float
// CC_Config_AUX_mode enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Float |  |  | 0 |  | Float
Diversion_Relay |  |  | 1 |  | Diversion: Relay
Diversion_Solid_St |  |  | 2 |  | Diversion: Solid St
Low_Batt_Disconnect |  |  | 3 |  | Low Batt Disconnect
Remote |  |  | 4 |  | Remote
Vent_Fan |  |  | 5 |  | Vent Fan
PV_Trigger |  |  | 6 |  | PV Trigger
Error_Output |  |  | 7 |  | Alarm Output
Night_Light |  |  | 8 |  | Night Light
// CC_Config_AUX_control enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Off |  |  | 0 |  | Off
Auto |  |  | 1 |  | Auto
On |  |  | 2 |  | On
// CC_Config_AUX_state enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Disabled |  |  | 0 |  | Disabled
Enabled |  |  | 1 |  | Enabled
// CC_Config_AUX_polarity enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
Low |  |  | 0 |  | Low
High |  |  | 1 |  | High